## S&C "TXP" Speed
S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter
S&C "TXP" Speed | [11 empty] | S&C "TXP" Speed | [11 empty] | S&C "TXP" Speed | [11 empty] | S&C "TXP" Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated April 11, 2025
Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information.
2TXP |  |  |  | 3TXP |  |  |  | 5TXP |  |  |  | 6TXP |  |  |  | 7TXP |  |  |  | 8TXP |  |  |  | 10TXP |  |  |  | 12TXP |  |  |  | 15TXP |  |  |  | 20TXP
Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s
3 | 671.3818 | 4 | 671.3983 | 5 | 671.3818 | 6 | 671.3983 | 9 | 671.3818 | 10 | 671.3983 | 10.8 | 671.3818 | 12 | 671.3983 | 12.6 | 671.3818 | 14 | 671.3983 | 14.4 | 671.3818 | 16 | 671.3983 | 18 | 671.3818 | 20 | 671.3983 | 21.6 | 671.3818 | 24 | 671.3983 | 27 | 671.3818 | 30 | 671.3983 | 36 | 671.3818 | 40 | 671.3983
4 | 260.075 | 5 | 260.0913 | 6 | 339.7808 | 7 | 339.7955 | 9.9 | 440.7174 | 11 | 440.733 | 11.7 | 471.3601 | 13 | 471.3768 | 13.5 | 494.9268 | 15 | 494.9434 | 15.3 | 513.5596 | 17 | 513.5768 | 18.9 | 541.137 | 21 | 541.1518 | 22.5 | 560.6661 | 25 | 560.683 | 27.9 | 581.0531 | 31 | 581.0684 | 36.9 | 602.0053 | 41 | 602.0184
5 | 137.3275 | 6 | 137.3413 | 7 | 207.4566 | 8 | 207.4705 | 10.8 | 300.045 | 12 | 300.0601 | 12.6 | 339.7806 | 14 | 339.7934 | 14.4 | 372.2299 | 16 | 372.2434 | 16.2 | 399.0534 | 18 | 399.0684 | 19.8 | 440.7174 | 22 | 440.733 | 23.4 | 471.3599 | 26 | 471.3768 | 28.8 | 504.7533 | 32 | 504.7684 | 37.8 | 541.1369 | 42 | 541.1518
6 | 80.04 | 7 | 80.0538 | 8 | 137.3271 | 9 | 137.3413 | 11.7 | 226.6653 | 13 | 226.683 | 13.5 | 260.0742 | 15 | 260.0913 | 15.3 | 287.8461 | 17 | 287.8601 | 17.1 | 314.2033 | 19 | 314.2184 | 20.7 | 362.1084 | 23 | 362.1247 | 24.3 | 399.0533 | 27 | 399.0684 | 29.7 | 440.7172 | 33 | 440.733 | 38.7 | 487.8042 | 43 | 487.8184
7 | 52.9156 | 8 | 52.9288 | 9 | 94.954 | 10 | 94.9684 | 12.6 | 174.8671 | 14 | 174.883 | 14.4 | 207.456 | 16 | 207.4705 | 16.2 | 235.5915 | 18 | 235.608 | 18 | 260.0743 | 20 | 260.0913 | 21.6 | 300.0448 | 24 | 300.0601 | 25.2 | 339.7804 | 28 | 339.7934 | 30.6 | 386.2388 | 34 | 386.2518 | 39.6 | 440.7172 | 44 | 440.733
8 | 39.6323 | 9 | 39.6455 | 9.9 | 68.0068 | 11 | 68.0205 | 13.5 | 137.3266 | 15 | 137.3413 | 15.3 | 167.7609 | 17 | 167.7747 | 17.1 | 194.9817 | 19 | 194.9955 | 18.9 | 219.2038 | 21 | 219.2184 | 22.5 | 260.0742 | 25 | 260.0913 | 26.1 | 292.8189 | 29 | 292.833 | 31.5 | 339.7802 | 35 | 339.7934 | 40.5 | 399.0532 | 45 | 399.0684
9 | 30.6037 | 10 | 30.6184 | 10.8 | 52.9153 | 12 | 52.9288 | 14.4 | 109.5484 | 16 | 109.5622 | 16.2 | 137.3266 | 18 | 137.3413 | 18 | 162.924 | 20 | 162.9413 | 19.8 | 186.2497 | 22 | 186.2663 | 23.4 | 226.6651 | 26 | 226.683 | 27 | 260.0741 | 30 | 260.0913 | 32.4 | 300.0446 | 36 | 300.058 | 41.4 | 362.1082 | 46 | 362.1247
9.9 | 25.467 | 11 | 25.483 | 11.7 | 43.478 | 13 | 43.4934 | 15.3 | 88.5936 | 17 | 88.608 | 17.1 | 113.6314 | 19 | 113.6455 | 18.9 | 137.3267 | 21 | 137.3413 | 20.7 | 159.3955 | 23 | 159.4101 | 24.3 | 198.6164 | 27 | 198.633 | 27.9 | 231.832 | 31 | 231.8497 | 33.3 | 272.5572 | 37 | 272.5747 | 42.3 | 329.2786 | 47 | 329.2934
10.8 | 21.6248 | 12 | 21.6413 | 12.6 | 36.2486 | 14 | 36.2622 | 16.2 | 72.5189 | 18 | 72.533 | 18 | 94.9537 | 20 | 94.9684 | 19.8 | 116.6765 | 22 | 116.6913 | 21.6 | 137.3266 | 24 | 137.3413 | 25.2 | 174.8669 | 28 | 174.883 | 28.8 | 207.4558 | 32 | 207.4705 | 34.2 | 248.2429 | 38 | 248.258 | 43.2 | 300.0446 | 48 | 300.058
11.7 | 18.6045 | 13 | 18.6184 | 13.5 | 30.6032 | 15 | 30.6184 | 17.1 | 60.0135 | 19 | 60.0268 | 18.9 | 80.0394 | 21 | 80.0538 | 20.7 | 99.8598 | 23 | 99.8747 | 22.5 | 119.0349 | 25 | 119.0497 | 26.1 | 154.6367 | 29 | 154.6518 | 29.7 | 186.2495 | 33 | 186.2663 | 35.1 | 226.665 | 39 | 226.683 | 44.1 | 279.0849 | 49 | 279.0997
12.6 | 16.1857 | 14 | 16.1997 | 14.4 | 26.9833 | 16 | 26.9997 | 18 | 52.915 | 20 | 52.9288 | 19.8 | 68.0066 | 22 | 68.0205 | 21.6 | 86.0327 | 24 | 86.0455 | 23.4 | 103.7581 | 26 | 103.7747 | 27 | 137.3264 | 30 | 137.3413 | 30.6 | 167.7607 | 34 | 167.7747 | 36 | 207.4558 | 40 | 207.4705 | 45 | 260.074 | 50 | 260.0913
13.5 | 14.2174 | 15 | 14.233 | 15.3 | 24.077 | 17 | 24.0913 | 18.9 | 46.9435 | 21 | 46.958 | 20.7 | 58.738 | 23 | 58.7518 | 22.5 | 74.5725 | 25 | 74.5851 | 24.3 | 90.9112 | 27 | 90.9247 | 27.9 | 122.421 | 31 | 122.4351 | 31.5 | 151.5573 | 35 | 151.5747 | 36.9 | 190.2401 | 41 | 190.258 | 45.9 | 242.643 | 51 | 242.658
14.4 | 12.5938 | 16 | 12.608 | 16.2 | 21.6244 | 18 | 21.6413 | 19.8 | 41.8791 | 22 | 41.8934 | 21.6 | 52.915 | 24 | 52.9288 | 23.4 | 65.0046 | 26 | 65.0184 | 25.2 | 80.0393 | 28 | 80.0538 | 28.8 | 109.5482 | 32 | 109.5622 | 32.4 | 137.3264 | 36 | 137.3413 | 37.8 | 174.8668 | 42 | 174.883 | 46.8 | 226.6649 | 52 | 226.6788
15.3 | 11.2377 | 17 | 11.2518 | 17.1 | 19.5351 | 19 | 19.5497 | 20.7 | 37.5515 | 23 | 37.5663 | 22.5 | 47.8708 | 25 | 47.8851 | 24.3 | 57.8544 | 27 | 57.8684 | 26.1 | 70.785 | 29 | 70.7997 | 29.7 | 98.3499 | 33 | 98.3663 | 33.3 | 124.7551 | 37 | 124.7684 | 38.7 | 161.0242 | 43 | 161.0413 | 47.7 | 212.0567 | 53 | 212.0705
16.2 | 10.0936 | 18 | 10.108 | 18 | 17.74 | 20 | 17.7538 | 21.6 | 33.8274 | 24 | 33.8413 | 23.4 | 43.4777 | 26 | 43.4913 | 25.2 | 52.9149 | 28 | 52.9288 | 27 | 62.8614 | 30 | 62.8768 | 30.6 | 88.5934 | 34 | 88.608 | 34.2 | 113.6311 | 38 | 113.6455 | 39.6 | 148.5785 | 44 | 148.5934 | 48.6 | 198.6163 | 54 | 198.633
17.1 | 9.0528 | 19 | 9.0663 | 18.9 | 16.1855 | 21 | 16.1997 | 22.5 | 30.6031 | 25 | 30.6184 | 24.3 | 39.6317 | 27 | 39.6455 | 26.1 | 48.5476 | 29 | 48.5622 | 27.9 | 57.2009 | 31 | 57.2163 | 31.5 | 80.0391 | 35 | 80.0538 | 35.1 | 103.758 | 39 | 103.7747 | 40.5 | 137.3264 | 45 | 137.3413 | 49.5 | 186.2495 | 55 | 186.2663
18 | 8.16 | 20 | 8.1747 | 19.8 | 14.8307 | 22 | 14.8434 | 23.4 | 28.2989 | 26 | 28.3122 | 25.2 | 36.2483 | 28 | 36.2622 | 27 | 44.6729 | 30 | 44.6872 | 28.8 | 52.9148 | 32 | 52.9288 | 32.4 | 72.5187 | 36 | 72.533 | 36 | 94.9533 | 40 | 94.9684 | 41.4 | 127.1511 | 46 | 127.1663 | 50.4 | 174.8668 | 56 | 174.883
18.9 | 7.3925 | 21 | 7.408 | 20.7 | 13.642 | 23 | 13.658 | 24.3 | 26.3608 | 27 | 26.3747 | 26.1 | 33.2577 | 29 | 33.2747 | 27.9 | 41.219 | 31 | 41.233 | 29.7 | 49.0647 | 33 | 49.0788 | 33.3 | 65.8846 | 37 | 65.8997 | 36.9 | 87.0836 | 41 | 87.0997 | 42.3 | 117.9307 | 47 | 117.9455 | 51.3 | 164.3355 | 57 | 164.3497
19.8 | 6.7282 | 22 | 6.7434 | 21.6 | 12.5936 | 24 | 12.608 | 25.2 | 24.6187 | 28 | 24.633 | 27 | 30.603 | 30 | 30.6163 | 28.8 | 38.1294 | 32 | 38.1434 | 30.6 | 45.599 | 34 | 45.6163 | 34.2 | 60.0134 | 38 | 60.0268 | 37.8 | 80.0392 | 42 | 80.0538 | 43.2 | 109.5482 | 48 | 109.5622 | 52.2 | 154.6366 | 58 | 154.6518
20.7 | 6.1492 | 23 | 6.1663 | 22.5 | 11.6637 | 25 | 11.6768 | 26.1 | 23.0472 | 29 | 23.0601 | 27.9 | 28.6425 | 31 | 28.658 | 29.7 | 35.3567 | 33 | 35.3705 | 31.5 | 42.4682 | 35 | 42.483 | 35.1 | 56.306 | 39 | 56.3205 | 38.7 | 73.7079 | 43 | 73.7247 | 44.1 | 101.9151 | 49 | 101.9288 | 53.1 | 145.6576 | 59 | 145.6747
21.6 | 5.6419 | 24 | 5.658 | 23.4 | 10.8351 | 26 | 10.8497 | 27 | 21.6243 | 30 | 21.6413 | 28.8 | 26.983 | 32 | 26.9997 | 30.6 | 32.8594 | 34 | 32.8747 | 32.4 | 39.6315 | 36 | 39.6455 | 36 | 52.9148 | 40 | 52.9288 | 39.6 | 68.0063 | 44 | 68.0205 | 45 | 94.9532 | 50 | 94.9684 | 54 | 137.3263 | 60 | 137.3413
22.5 | 5.1946 | 25 | 5.208 | 24.3 | 10.0935 | 27 | 10.108 | 27.9 | 20.3319 | 31 | 20.3455 | 29.7 | 25.4665 | 33 | 25.483 | 31.5 | 30.603 | 35 | 30.6163 | 33.3 | 37.0556 | 37 | 37.0684 | 36.9 | 49.8025 | 41 | 49.8163 | 40.5 | 62.8614 | 45 | 62.8747 | 45.9 | 88.5934 | 51 | 88.608 | 54.9 | 129.5958 | 61 | 129.6101
23.4 | 4.7984 | 26 | 4.8122 | 25.2 | 9.3829 | 28 | 9.3997 | 28.8 | 19.1542 | 32 | 19.1684 | 30.6 | 24.0768 | 34 | 24.0913 | 32.4 | 28.8922 | 36 | 28.908 | 34.2 | 34.7079 | 38 | 34.7247 | 37.8 | 46.9433 | 42 | 46.958 | 41.4 | 58.7378 | 46 | 58.7518 | 46.8 | 82.7681 | 52 | 82.783 | 55.8 | 122.4209 | 62 | 122.4351
24.3 | 4.4458 | 27 | 4.4601 | 26.1 | 8.7394 | 29 | 8.7538 | 29.7 | 18.0779 | 33 | 18.0913 | 31.5 | 22.8004 | 35 | 22.8163 | 33.3 | 27.4418 | 37 | 27.458 | 35.1 | 32.5652 | 39 | 32.5788 | 38.7 | 44.3087 | 43 | 44.3247 | 42.3 | 55.7201 | 47 | 55.7351 | 47.7 | 77.4254 | 53 | 77.4413 | 56.7 | 115.7588 | 63 | 115.7747
25.2 | 4.1305 | 28 | 4.1434 | 27 | 8.1597 | 30 | 8.1747 | 30.6 | 17.0915 | 34 | 17.108 | 32.4 | 21.6242 | 36 | 21.6413 | 34.2 | 26.1003 | 38 | 26.1163 | 36 | 30.603 | 40 | 30.6163 | 39.6 | 41.8788 | 44 | 41.8934 | 43.2 | 52.9148 | 48 | 52.9288 | 48.6 | 72.5186 | 54 | 72.533 | 57.6 | 109.5481 | 64 | 109.5622
26.1 | 3.8476 | 29 | 3.8622 | 27.9 | 7.6356 | 31 | 7.6497 | 31.5 | 16.1853 | 35 | 16.1997 | 33.3 | 20.539 | 37 | 20.5538 | 35.1 | 24.8563 | 39 | 24.8705 | 36.9 | 29.082 | 41 | 29.0955 | 40.5 | 39.6315 | 45 | 39.6455 | 44.1 | 50.3038 | 49 | 50.3184 | 49.5 | 68.0062 | 55 | 68.0205 | 58.5 | 103.7578 | 65 | 103.7747
27 | 3.5927 | 30 | 3.608 | 28.8 | 7.1603 | 32 | 7.1747 | 32.4 | 15.3508 | 36 | 15.3663 | 34.2 | 19.5348 | 38 | 19.5497 | 36 | 23.7014 | 40 | 23.7163 | 37.8 | 27.7938 | 42 | 27.808 | 41.4 | 37.5514 | 46 | 37.5663 | 45 | 47.8707 | 50 | 47.8851 | 50.4 | 63.8473 | 56 | 63.8601 | 59.4 | 98.3499 | 66 | 98.3663
27.9 | 3.3623 | 31 | 3.3768 | 29.7 | 6.728 | 33 | 6.7413 | 33.3 | 14.5804 | 37 | 14.5934 | 35.1 | 18.6042 | 39 | 18.6184 | 36.9 | 22.6264 | 41 | 22.6413 | 38.7 | 26.5916 | 43 | 26.608 | 42.3 | 35.621 | 47 | 35.6351 | 45.9 | 45.599 | 51 | 45.6163 | 51.3 | 60.0132 | 57 | 60.0268 | 60.3 | 93.3063 | 67 | 93.3205
28.8 | 3.1534 | 32 | 3.1684 | 30.6 | 6.3334 | 34 | 6.3497 | 34.2 | 13.8677 | 38 | 13.883 | 36 | 17.7397 | 40 | 17.7538 | 37.8 | 21.6242 | 42 | 21.6413 | 39.6 | 25.4665 | 44 | 25.483 | 43.2 | 33.8272 | 48 | 33.8413 | 46.8 | 43.4774 | 52 | 43.4913 | 52.2 | 57.5034 | 58 | 57.5184 | 61.2 | 88.5933 | 68 | 88.608
29.7 | 2.9633 | 33 | 2.9768 | 31.5 | 5.9726 | 35 | 5.9872 | 35.1 | 13.2069 | 39 | 13.2205 | 36.9 | 16.9352 | 41 | 16.9497 | 38.7 | 20.6888 | 43 | 20.7018 | 40.5 | 24.4131 | 45 | 24.4268 | 44.1 | 32.1583 | 49 | 32.1747 | 47.7 | 41.4923 | 53 | 41.508 | 53.1 | 55.1408 | 59 | 55.158 | 62.1 | 84.1751 | 69 | 84.1913
30.6 | 2.7898 | 34 | 2.8038 | 32.4 | 5.6417 | 36 | 5.658 | 36 | 12.5934 | 40 | 12.608 | 37.8 | 16.1853 | 42 | 16.1997 | 39.6 | 19.8138 | 44 | 19.8268 | 41.4 | 23.4254 | 46 | 23.4413 | 45 | 30.6029 | 50 | 30.6163 | 48.6 | 39.6315 | 54 | 39.6455 | 54 | 52.9147 | 60 | 52.9288 | 63 | 80.039 | 70 | 80.0518
31.5 | 2.6312 | 35 | 2.6455 | 33.3 | 5.3375 | 37 | 5.3518 | 36.9 | 12.0225 | 41 | 12.0372 | 38.7 | 15.4852 | 43 | 15.4997 | 40.5 | 18.9945 | 45 | 19.008 | 42.3 | 22.4974 | 47 | 22.5101 | 45.9 | 29.3502 | 51 | 29.3663 | 49.5 | 37.8868 | 55 | 37.9018 | 54.9 | 50.8106 | 61 | 50.8247 | 63.9 | 76.1607 | 71 | 76.1747
32.4 | 2.4857 | 36 | 2.4997 | 34.2 | 5.0572 | 38 | 5.0705 | 37.8 | 11.4902 | 42 | 11.5038 | 39.6 | 14.8304 | 44 | 14.8434 | 41.4 | 18.2256 | 46 | 18.2413 | 43.2 | 21.6242 | 48 | 21.6413 | 46.8 | 28.2986 | 52 | 28.3122 | 50.4 | 36.2482 | 56 | 36.2622 | 55.8 | 48.8228 | 62 | 48.8372 | 64.8 | 72.5186 | 72 | 72.533
33.3 | 2.352 | 37 | 2.3663 | 35.1 | 4.7983 | 39 | 4.8122 | 38.7 | 10.9933 | 43 | 11.008 | 40.5 | 14.2172 | 45 | 14.233 | 42.3 | 17.5039 | 47 | 17.5184 | 44.1 | 20.8024 | 49 | 20.8163 | 47.7 | 27.3032 | 53 | 27.3184 | 51.3 | 34.7078 | 57 | 34.7247 | 56.7 | 46.9432 | 63 | 46.958 | 65.7 | 69.1021 | 73 | 69.1163
34.2 | 2.2287 | 38 | 2.2434 | 36 | 4.5588 | 40 | 4.5747 | 39.6 | 10.5285 | 44 | 10.5434 | 41.4 | 13.6418 | 46 | 13.658 | 43.2 | 16.8248 | 48 | 16.8413 | 45 | 20.0273 | 50 | 20.0413 | 48.6 | 26.3606 | 54 | 26.3747 | 52.2 | 33.2575 | 58 | 33.2747 | 57.6 | 45.163 | 64 | 45.1768 | 66.6 | 65.8844 | 74 | 65.8997
35.1 | 2.115 | 39 | 2.1288 | 36.9 | 4.3367 | 41 | 4.3518 | 40.5 | 10.0933 | 45 | 10.108 | 42.3 | 13.1016 | 47 | 13.1163 | 44.1 | 16.1853 | 49 | 16.1997 | 45.9 | 19.2956 | 51 | 19.3101 | 49.5 | 25.4665 | 55 | 25.483 | 53.1 | 31.8918 | 59 | 31.908 | 58.5 | 43.4774 | 65 | 43.4913 | 67.5 | 62.8611 | 75 | 62.8747
36 | 2.0096 | 40 | 2.0247 | 37.8 | 4.1304 | 42 | 4.1434 | 41.4 | 9.6602 | 46 | 9.6747 | 43.2 | 12.5934 | 48 | 12.608 | 45 | 15.5822 | 50 | 15.5955 | 46.8 | 18.604 | 52 | 18.6184 | 50.4 | 24.6186 | 56 | 24.633 | 54 | 30.6029 | 60 | 30.6163 | 59.4 | 41.8787 | 66 | 41.8934 | 68.4 | 60.0131 | 76 | 60.0268
36.9 | 1.9133 | 41 | 1.9268 | 38.7 | 3.9385 | 43 | 3.9518 | 42.3 | 9.2486 | 47 | 9.2622 | 44.1 | 12.1147 | 49 | 12.1288 | 45.9 | 15.013 | 51 | 15.0268 | 47.7 | 17.9498 | 53 | 17.9663 | 51.3 | 23.8132 | 57 | 23.8268 | 54.9 | 29.5313 | 61 | 29.5455 | 60.3 | 40.3615 | 67 | 40.3768 | 69.3 | 58.1185 | 77 | 58.133
37.8 | 1.8236 | 42 | 1.8372 | 39.6 | 3.7596 | 44 | 3.7747 | 43.2 | 8.8626 | 48 | 8.8768 | 45 | 11.6635 | 50 | 11.6768 | 46.8 | 14.4751 | 52 | 14.4913 | 48.6 | 17.3301 | 54 | 17.3434 | 52.2 | 23.0471 | 58 | 23.0601 | 55.8 | 28.6424 | 62 | 28.658 | 61.2 | 38.9205 | 68 | 38.9351 | 70.2 | 56.3058 | 78 | 56.3184
38.7 | 1.7403 | 43 | 1.7538 | 40.5 | 3.5927 | 45 | 3.608 | 44.1 | 8.5003 | 49 | 8.5163 | 45.9 | 11.2375 | 51 | 11.2518 | 47.7 | 13.966 | 53 | 13.983 | 49.5 | 16.7426 | 55 | 16.758 | 53.1 | 22.3185 | 59 | 22.333 | 56.7 | 27.7937 | 63 | 27.808 | 62.1 | 37.5513 | 69 | 37.5663 | 71.1 | 54.5735 | 79 | 54.5872
39.6 | 1.6624 | 44 | 1.6768 | 41.4 | 3.4365 | 46 | 3.4518 | 45 | 8.1596 | 50 | 8.1747 | 46.8 | 10.8349 | 52 | 10.8497 | 48.6 | 13.484 | 54 | 13.4997 | 50.4 | 16.1852 | 56 | 16.1997 | 54 | 21.6242 | 60 | 21.6413 | 57.6 | 26.9829 | 64 | 26.9997 | 63 | 36.2481 | 70 | 36.2622 | 72 | 52.9147 | 80 | 52.9288
40.5 | 1.5898 | 45 | 1.6038 | 42.3 | 3.2904 | 47 | 3.3038 | 45.9 | 7.8389 | 51 | 7.8518 | 47.7 | 10.454 | 53 | 10.4684 | 49.5 | 13.0269 | 55 | 13.0413 | 51.3 | 15.6557 | 57 | 15.6684 | 54.9 | 20.9627 | 61 | 20.9768 | 58.5 | 26.2082 | 65 | 26.2247 | 63.9 | 35.0083 | 71 | 35.0247 | 72.9 | 51.3255 | 81 | 51.3413
41.4 | 1.5219 | 46 | 1.5351 | 43.2 | 3.1533 | 48 | 3.1684 | 46.8 | 7.5367 | 52 | 7.5518 | 48.6 | 10.0933 | 54 | 10.108 | 50.4 | 12.5934 | 56 | 12.608 | 52.2 | 15.1522 | 58 | 15.1663 | 55.8 | 20.3318 | 62 | 20.3455 | 59.4 | 25.4664 | 66 | 25.483 | 64.8 | 33.8271 | 72 | 33.8413 | 73.8 | 49.8024 | 82 | 49.8163
42.3 | 1.4582 | 47 | 1.4747 | 44.1 | 3.0246 | 49 | 3.0413 | 47.7 | 7.2517 | 53 | 7.2663 | 49.5 | 9.7314 | 55 | 9.7455 | 51.3 | 12.1814 | 57 | 12.1955 | 53.1 | 14.6732 | 59 | 14.6872 | 56.7 | 19.7297 | 63 | 19.7434 | 60.3 | 24.7567 | 67 | 24.7705 | 65.7 | 32.702 | 73 | 32.7163 | 74.7 | 48.342 | 83 | 48.358
43.2 | 1.3984 | 48 | 1.4122 | 45 | 2.9036 | 50 | 2.9184 | 48.6 | 6.9824 | 54 | 6.9997 | 50.4 | 9.3828 | 56 | 9.3997 | 52.2 | 11.7897 | 58 | 11.8038 | 54 | 14.2171 | 60 | 14.233 | 57.6 | 19.1541 | 64 | 19.1684 | 61.2 | 24.0767 | 68 | 24.0913 | 66.6 | 31.6279 | 74 | 31.6413 | 75.6 | 46.9432 | 84 | 46.958
44.1 | 1.3423 | 49 | 1.358 | 45.9 | 2.7898 | 51 | 2.8038 | 49.5 | 6.7279 | 55 | 6.7413 | 51.3 | 9.0525 | 57 | 9.0663 | 53.1 | 11.417 | 59 | 11.433 | 54.9 | 13.7822 | 61 | 13.7955 | 58.5 | 18.604 | 65 | 18.6184 | 62.1 | 23.4253 | 69 | 23.4413 | 67.5 | 30.6029 | 75 | 30.6163 | 76.5 | 45.599 | 85 | 45.6163
45 | 1.2895 | 50 | 1.3038 | 46.8 | 2.6825 | 52 | 2.6997 | 50.4 | 6.487 | 56 | 6.5018 | 52.2 | 8.7392 | 58 | 8.7538 | 54 | 11.0621 | 60 | 11.0768 | 55.8 | 13.3675 | 62 | 13.383 | 59.4 | 18.0777 | 66 | 18.0913 | 63 | 22.8003 | 70 | 22.8163 | 68.4 | 29.7146 | 76 | 29.7288 | 77.4 | 44.3085 | 86 | 44.3247
45.9 | 1.2398 | 51 | 1.2538 | 47.7 | 2.5813 | 53 | 2.5955 | 51.3 | 6.2587 | 57 | 6.2747 | 53.1 | 8.442 | 59 | 8.458 | 54.9 | 10.7239 | 61 | 10.7413 | 56.7 | 12.9715 | 63 | 12.9851 | 60.3 | 17.5741 | 67 | 17.5913 | 63.9 | 22.2004 | 71 | 22.2163 | 69.3 | 28.9931 | 77 | 29.008 | 78.3 | 43.0693 | 87 | 43.083
46.8 | 1.1929 | 52 | 1.208 | 48.6 | 2.4857 | 54 | 2.4997 | 52.2 | 6.0423 | 58 | 6.058 | 54 | 8.1596 | 60 | 8.1747 | 55.8 | 10.4012 | 62 | 10.4163 | 57.6 | 12.5933 | 64 | 12.608 | 61.2 | 17.0915 | 68 | 17.108 | 64.8 | 21.6241 | 72 | 21.6413 | 70.2 | 28.2986 | 78 | 28.3122 | 79.2 | 41.8787 | 88 | 41.8934
47.7 | 1.1487 | 53 | 1.1622 | 49.5 | 2.3953 | 55 | 2.4101 | 53.1 | 5.8368 | 59 | 5.8518 | 54.9 | 7.8911 | 61 | 7.908 | 56.7 | 10.0933 | 63 | 10.108 | 58.5 | 12.2317 | 65 | 12.2455 | 62.1 | 16.6288 | 69 | 16.6434 | 65.7 | 21.0707 | 73 | 21.0851 | 71.1 | 27.6285 | 79 | 27.6434 | 80.1 | 40.7329 | 89 | 40.7497
48.6 | 1.1069 | 54 | 1.1205 | 50.4 | 2.3097 | 56 | 2.3247 | 54 | 5.6417 | 60 | 5.658 | 55.8 | 7.6355 | 62 | 7.6497 | 57.6 | 9.7828 | 64 | 9.7997 | 59.4 | 11.8857 | 66 | 11.8997 | 63 | 16.1852 | 70 | 16.1997 | 66.6 | 20.5389 | 74 | 20.5518 | 72 | 26.9829 | 80 | 26.9997 | 81 | 39.6314 | 90 | 39.6455
49.5 | 1.0674 | 55 | 1.083 | 51.3 | 2.2287 | 57 | 2.2434 | 54.9 | 5.4561 | 61 | 5.4705 | 56.7 | 7.3922 | 63 | 7.408 | 58.5 | 9.4804 | 65 | 9.4934 | 60.3 | 11.5546 | 67 | 11.5684 | 63.9 | 15.7593 | 71 | 15.7747 | 67.5 | 20.0272 | 75 | 20.0413 | 72.9 | 26.3605 | 81 | 26.3747 | 81.9 | 38.5719 | 91 | 38.5851
50.4 | 1.0299 | 56 | 1.0434 | 52.2 | 2.1518 | 58 | 2.1663 | 55.8 | 5.2795 | 62 | 5.2934 | 57.6 | 7.1602 | 64 | 7.1747 | 59.4 | 9.1919 | 66 | 9.208 | 61.2 | 11.2374 | 68 | 11.2518 | 64.8 | 15.3506 | 72 | 15.3663 | 68.4 | 19.5347 | 76 | 19.5497 | 73.8 | 25.7592 | 82 | 25.7747 | 82.8 | 37.5513 | 92 | 37.5663
51.3 | 0.99443 | 57 | 1.008 | 53.1 | 2.0788 | 59 | 2.0934 | 56.7 | 5.1113 | 63 | 5.1247 | 58.5 | 6.939 | 65 | 6.9518 | 60.3 | 8.9162 | 67 | 8.933 | 62.1 | 10.9334 | 69 | 10.9497 | 65.7 | 14.9577 | 73 | 14.9747 | 69.3 | 19.0606 | 77 | 19.0747 | 74.7 | 25.1791 | 83 | 25.1934 | 83.7 | 36.5677 | 93 | 36.583
52.2 | 0.96076 | 58 | 0.9747 | 54 | 2.0095 | 60 | 2.0247 | 57.6 | 4.9511 | 64 | 4.9663 | 59.4 | 6.7279 | 66 | 6.7413 | 61.2 | 8.6527 | 68 | 8.6663 | 63 | 10.6417 | 70 | 10.658 | 66.6 | 14.5802 | 74 | 14.5934 | 70.2 | 18.604 | 78 | 18.6184 | 75.6 | 24.6185 | 84 | 24.633 | 84.6 | 35.6208 | 94 | 35.6351
53.1 | 0.92879 | 59 | 0.9434 | 54.9 | 1.9445 | 61 | 1.958 | 58.5 | 4.7982 | 65 | 4.8122 | 60.3 | 6.5262 | 67 | 6.5413 | 62.1 | 8.4007 | 69 | 8.4163 | 63.9 | 10.3619 | 71 | 10.3768 | 67.5 | 14.217 | 75 | 14.233 | 71.1 | 18.1638 | 79 | 18.1768 | 76.5 | 24.0767 | 85 | 24.0913 | 85.5 | 34.7078 | 95 | 34.7247
54 | 0.8984 | 60 | 0.9122 | 55.8 | 1.8826 | 62 | 1.8997 | 59.4 | 4.6523 | 66 | 4.6663 | 61.2 | 6.3334 | 68 | 6.3497 | 63 | 8.1595 | 70 | 8.1747 | 64.8 | 10.0932 | 72 | 10.108 | 68.4 | 13.8676 | 76 | 13.883 | 72 | 17.7395 | 80 | 17.7538 | 77.4 | 23.5533 | 86 | 23.5684 | 86.4 | 33.8271 | 96 | 33.8413
54.9 | 0.86949 | 61 | 0.883 | 56.7 | 1.8236 | 63 | 1.8372 | 60.3 | 4.5129 | 67 | 4.5268 | 62.1 | 6.149 | 69 | 6.1663 | 63.9 | 7.9285 | 71 | 7.9434 | 65.7 | 9.8216 | 73 | 9.8351 | 69.3 | 13.531 | 77 | 13.5455 | 72.9 | 17.3301 | 81 | 17.3434 | 78.3 | 23.047 | 87 | 23.0601 | 87.3 | 32.9783 | 97 | 32.9934
55.8 | 0.84198 | 62 | 0.858 | 57.6 | 1.7673 | 64 | 1.783 | 61.2 | 4.3797 | 68 | 4.3934 | 63 | 5.9725 | 70 | 5.9872 | 64.8 | 7.7072 | 72 | 7.7247 | 66.6 | 9.5547 | 74 | 9.5684 | 70.2 | 13.2068 | 78 | 13.2205 | 73.8 | 16.935 | 82 | 16.9497 | 79.2 | 22.5575 | 88 | 22.5747 | 88.2 | 32.1582 | 98 | 32.1747
56.7 | 0.81575 | 63 | 0.833 | 58.5 | 1.7136 | 65 | 1.7268 | 62.1 | 4.2523 | 69 | 4.2663 | 63.9 | 5.8036 | 71 | 5.8184 | 65.7 | 7.495 | 73 | 7.5101 | 67.5 | 9.2985 | 75 | 9.3122 | 71.1 | 12.8945 | 79 | 12.908 | 74.7 | 16.5537 | 83 | 16.5684 | 80.1 | 22.0831 | 89 | 22.0997 | 89.1 | 31.3674 | 99 | 31.383
57.6 | 0.79074 | 64 | 0.808 | 59.4 | 1.6624 | 66 | 1.6768 | 63 | 4.1303 | 70 | 4.1434 | 64.8 | 5.6416 | 72 | 5.658 | 66.6 | 7.2914 | 74 | 7.308 | 68.4 | 9.0524 | 76 | 9.0663 | 72 | 12.5933 | 80 | 12.608 | 75.6 | 16.1852 | 84 | 16.1997 | 81 | 21.6241 | 90 | 21.6413 | 90 | 30.6028 | 100 | 30.6163
58.5 | 0.76687 | 65 | 0.783 | 60.3 | 1.6134 | 67 | 1.6268 | 63.9 | 4.0135 | 71 | 4.0268 | 65.7 | 5.4863 | 73 | 5.4997 | 67.5 | 7.0959 | 75 | 7.1101 | 69.3 | 8.816 | 77 | 8.833 | 72.9 | 12.3027 | 81 | 12.3163 | 76.5 | 15.8292 | 85 | 15.8434 | 81.9 | 21.1798 | 91 | 21.1934 | 90.9 | 29.8994 | 101 | 29.9163
59.4 | 0.7441 | 66 | 0.758 | 61.2 | 1.5666 | 68 | 1.583 | 64.8 | 3.9016 | 72 | 3.9163 | 66.6 | 5.3374 | 74 | 5.3518 | 68.4 | 6.9082 | 76 | 6.9247 | 70.2 | 8.5887 | 78 | 8.6018 | 73.8 | 12.0223 | 82 | 12.0351 | 77.4 | 15.485 | 86 | 15.4997 | 82.8 | 20.7492 | 92 | 20.7663 | 91.8 | 29.3501 | 102 | 29.3663
60.3 | 0.7223 | 67 | 0.7351 | 62.1 | 1.5218 | 69 | 1.5351 | 65.7 | 3.7943 | 73 | 3.808 | 67.5 | 5.1944 | 75 | 5.208 | 69.3 | 6.7279 | 77 | 6.7413 | 71.1 | 8.37 | 79 | 8.3851 | 74.7 | 11.7515 | 83 | 11.7663 | 78.3 | 15.1521 | 87 | 15.1663 | 83.7 | 20.3317 | 93 | 20.3455 | 92.7 | 28.8169 | 103 | 28.833
61.2 | 0.70149 | 68 | 0.7163 | 63 | 1.4788 | 70 | 1.4934 | 66.6 | 3.6914 | 74 | 3.708 | 68.4 | 5.057 | 76 | 5.0705 | 70.2 | 6.5544 | 78 | 6.5684 | 72 | 8.1595 | 80 | 8.1747 | 75.6 | 11.4901 | 84 | 11.5038 | 79.2 | 14.8303 | 88 | 14.8434 | 84.6 | 19.9272 | 94 | 19.9413 | 93.6 | 28.2985 | 104 | 28.3122
62.1 | 0.68159 | 69 | 0.6955 | 63.9 | 1.4378 | 71 | 1.4518 | 67.5 | 3.5926 | 75 | 3.608 | 69.3 | 4.9251 | 77 | 4.9413 | 71.1 | 6.3876 | 79 | 6.4018 | 72.9 | 7.9569 | 81 | 7.9705 | 76.5 | 11.2374 | 85 | 11.2518 | 80.1 | 14.5187 | 89 | 14.533 | 85.5 | 19.5346 | 95 | 19.5497 | 94.5 | 27.7936 | 105 | 27.808
63 | 0.6625 | 70 | 0.6768 | 64.8 | 1.3984 | 72 | 1.4122 | 68.4 | 3.4977 | 76 | 3.5122 | 70.2 | 4.7981 | 78 | 4.8122 | 72 | 6.227 | 80 | 6.2413 | 73.8 | 7.7616 | 82 | 7.7768 | 77.4 | 10.9932 | 86 | 11.008 | 81 | 14.217 | 90 | 14.233 | 86.4 | 19.154 | 96 | 19.1684 | 95.4 | 27.3031 | 106 | 27.3184
63.9 | 0.64425 | 71 | 0.658 | 65.7 | 1.3606 | 73 | 1.3747 | 69.3 | 3.4064 | 77 | 3.4205 | 71.1 | 4.6761 | 79 | 4.6913 | 72.9 | 6.0724 | 81 | 6.0872 | 74.7 | 7.5735 | 83 | 7.5872 | 78.3 | 10.7569 | 87 | 10.7705 | 81.9 | 13.9249 | 91 | 13.9413 | 87.3 | 18.7845 | 97 | 18.7997 | 96.3 | 26.8251 | 107 | 26.8413
64.8 | 0.62672 | 72 | 0.6413 | 66.6 | 1.3243 | 74 | 1.3413 | 70.2 | 3.3187 | 78 | 3.333 | 72 | 4.5586 | 80 | 4.5747 | 73.8 | 5.9235 | 82 | 5.9372 | 75.6 | 7.3921 | 84 | 7.408 | 79.2 | 10.5284 | 88 | 10.5434 | 82.8 | 13.6417 | 92 | 13.658 | 88.2 | 18.426 | 98 | 18.4413 | 97.2 | 26.3605 | 108 | 26.3747
65.7 | 0.60994 | 73 | 0.6247 | 67.5 | 1.2895 | 75 | 1.3038 | 71.1 | 3.2344 | 79 | 3.2497 | 72.9 | 4.4455 | 81 | 4.4601 | 74.7 | 5.78 | 83 | 5.7934 | 76.5 | 7.2171 | 85 | 7.233 | 80.1 | 10.3073 | 89 | 10.3247 | 83.7 | 13.3675 | 93 | 13.383 | 89.1 | 18.0777 | 99 | 18.0913 | 98.1 | 25.9075 | 109 | 25.9247
66.6 | 0.59383 | 74 | 0.608 | 68.4 | 1.256 | 76 | 1.2705 | 72 | 3.1532 | 80 | 3.1684 | 73.8 | 4.3366 | 82 | 4.3518 | 75.6 | 5.6416 | 84 | 5.658 | 77.4 | 7.0483 | 86 | 7.0622 | 81 | 10.0932 | 90 | 10.108 | 84.6 | 13.1014 | 94 | 13.1163 | 90 | 17.7395 | 100 | 17.7538 | 99 | 25.4664 | 110 | 25.483
67.5 | 0.57836 | 75 | 0.5934 | 69.3 | 1.2239 | 77 | 1.2372 | 72.9 | 3.075 | 81 | 3.0913 | 74.7 | 4.2316 | 83 | 4.2455 | 76.5 | 5.5081 | 85 | 5.5247 | 78.3 | 6.8852 | 87 | 6.8997 | 81.9 | 9.8763 | 91 | 9.8913 | 85.5 | 12.8434 | 95 | 12.858 | 90.9 | 17.4108 | 101 | 17.4247 | 99.9 | 25.0372 | 111 | 25.0518
68.4 | 0.56348 | 76 | 0.5768 | 70.2 | 1.1929 | 78 | 1.208 | 73.8 | 2.9997 | 82 | 3.0163 | 75.6 | 4.1303 | 84 | 4.1434 | 77.4 | 5.3793 | 86 | 5.3934 | 79.2 | 6.7278 | 88 | 6.7413 | 82.8 | 9.6601 | 92 | 9.6747 | 86.4 | 12.5933 | 96 | 12.608 | 91.8 | 17.0914 | 102 | 17.108 | 100.8 | 24.6185 | 112 | 24.633
69.3 | 0.54918 | 77 | 0.5663 | 71.1 | 1.1631 | 79 | 1.1768 | 74.7 | 2.9272 | 83 | 2.9413 | 76.5 | 4.0326 | 85 | 4.0497 | 78.3 | 5.2549 | 87 | 5.2684 | 80.1 | 6.5757 | 89 | 6.5913 | 83.7 | 9.4509 | 93 | 9.4663 | 87.3 | 12.3504 | 97 | 12.3663 | 92.7 | 16.7808 | 103 | 16.7955 | 101.7 | 24.2104 | 113 | 24.2247
70.2 | 0.53542 | 78 | 0.5497 | 72 | 1.1345 | 80 | 1.1497 | 75.6 | 2.8572 | 84 | 2.8747 | 77.4 | 3.9384 | 86 | 3.9518 | 79.2 | 5.1348 | 88 | 5.1497 | 81 | 6.4287 | 90 | 6.4434 | 84.6 | 9.2485 | 94 | 9.2622 | 88.2 | 12.1146 | 98 | 12.1288 | 93.6 | 16.4789 | 104 | 16.4934 | 102.6 | 23.8131 | 114 | 23.8268
71.1 | 0.5222 | 79 | 0.5351 | 72.9 | 1.1068 | 81 | 1.1205 | 76.5 | 2.7897 | 85 | 2.8038 | 78.3 | 3.8474 | 87 | 3.8622 | 80.1 | 5.0188 | 89 | 5.033 | 81.9 | 6.2865 | 91 | 6.3018 | 85.5 | 9.0524 | 95 | 9.0663 | 89.1 | 11.8857 | 99 | 11.8997 | 94.5 | 16.1851 | 105 | 16.1997 | 103.5 | 23.4252 | 115 | 23.4413
72 | 0.50945 | 80 | 0.5247 | 73.8 | 1.0802 | 82 | 1.0934 | 77.4 | 2.7246 | 86 | 2.7413 | 79.2 | 3.7595 | 88 | 3.7747 | 81 | 4.9066 | 90 | 4.9205 | 82.8 | 6.149 | 92 | 6.1663 | 86.4 | 8.8625 | 96 | 8.8768 | 90 | 11.6634 | 100 | 11.6768 | 95.4 | 15.8994 | 106 | 15.9163 | 104.4 | 23.047 | 116 | 23.0601
72.9 | 0.49716 | 81 | 0.5101 | 74.7 | 1.0546 | 83 | 1.0684 | 78.3 | 2.6617 | 87 | 2.6768 | 80.1 | 3.6746 | 89 | 3.6913 | 81.9 | 4.7982 | 91 | 4.8122 | 83.7 | 6.0159 | 93 | 6.033 | 87.3 | 8.6785 | 97 | 8.6934 | 90.9 | 11.4474 | 101 | 11.4601 | 96.3 | 15.6212 | 107 | 15.6351 | 105.3 | 22.678 | 117 | 22.6913
73.8 | 0.48534 | 82 | 0.4997 | 75.6 | 1.0299 | 84 | 1.0434 | 79.2 | 2.601 | 88 | 2.6163 | 81 | 3.5925 | 90 | 3.608 | 82.8 | 4.6932 | 92 | 4.708 | 84.6 | 5.8872 | 94 | 5.9018 | 88.2 | 8.5002 | 98 | 8.5163 | 91.8 | 11.2373 | 102 | 11.2518 | 97.2 | 15.3506 | 108 | 15.3663 | 106.2 | 22.3184 | 118 | 22.333
74.7 | 0.47396 | 83 | 0.4913 | 76.5 | 1.006 | 85 | 1.0205 | 80.1 | 2.5423 | 89 | 2.558 | 81.9 | 3.5132 | 91 | 3.5268 | 83.7 | 4.5917 | 93 | 4.608 | 85.5 | 5.7624 | 95 | 5.7768 | 89.1 | 8.3272 | 99 | 8.3413 | 92.7 | 11.0332 | 103 | 11.0497 | 98.1 | 15.0869 | 109 | 15.1018 | 107.1 | 21.967 | 119 | 21.983
75.6 | 0.46295 | 84 | 0.4768 | 77.4 | 0.98295 | 86 | 0.99967 | 81 | 2.4856 | 90 | 2.4997 | 82.8 | 3.4364 | 92 | 3.4497 | 84.6 | 4.4935 | 94 | 4.508 | 86.4 | 5.6416 | 96 | 5.658 | 90 | 8.1595 | 100 | 8.1747 | 93.6 | 10.8348 | 104 | 10.8497 | 99 | 14.8303 | 110 | 14.8434 | 108 | 21.6241 | 120 | 21.6413
76.5 | 0.45236 | 85 | 0.4663 | 78.3 | 0.96067 | 87 | 0.97467 | 81.9 | 2.4308 | 91 | 2.4455 | 83.7 | 3.3622 | 93 | 3.3768 | 85.5 | 4.3983 | 95 | 4.4122 | 87.3 | 5.5245 | 97 | 5.5413 | 90.9 | 7.9968 | 101 | 8.0101 | 94.5 | 10.6417 | 105 | 10.658 | 99.9 | 14.5802 | 111 | 14.5934 | 108.9 | 21.2896 | 121 | 21.3038
77.4 | 0.4421 | 86 | 0.458 | 79.2 | 0.93919 | 88 | 0.95384 | 82.8 | 2.3777 | 92 | 2.3913 | 84.6 | 3.2903 | 94 | 3.3038 | 86.4 | 4.3061 | 96 | 4.3205 | 88.2 | 5.4111 | 98 | 5.4247 | 91.8 | 7.8388 | 102 | 7.8518 | 95.4 | 10.4539 | 106 | 10.4684 | 100.8 | 14.3364 | 112 | 14.3497 | 109.8 | 20.9626 | 122 | 20.9768
78.3 | 0.43219 | 87 | 0.4455 | 80.1 | 0.91842 | 89 | 0.933 | 83.7 | 2.3264 | 93 | 2.3413 | 85.5 | 3.2207 | 95 | 3.2351 | 87.3 | 4.2169 | 97 | 4.233 | 89.1 | 5.3011 | 99 | 5.3163 | 92.7 | 7.6855 | 103 | 7.6997 | 96.3 | 10.2711 | 107 | 10.2851 | 101.7 | 14.099 | 113 | 14.1163 | 110.7 | 20.6437 | 123 | 20.658
79.2 | 0.42265 | 88 | 0.4372 | 81 | 0.89832 | 90 | 0.91217 | 84.6 | 2.2767 | 94 | 2.2913 | 86.4 | 3.1532 | 96 | 3.1684 | 88.2 | 4.1303 | 98 | 4.1434 | 90 | 5.1943 | 100 | 5.208 | 93.6 | 7.5367 | 104 | 7.5518 | 97.2 | 10.0932 | 108 | 10.108 | 102.6 | 13.8675 | 114 | 13.883 | 111.6 | 20.3317 | 124 | 20.3455
80.1 | 0.41342 | 89 | 0.4268 | 81.9 | 0.87893 | 91 | 0.89342 | 85.5 | 2.2286 | 95 | 2.2434 | 87.3 | 3.0879 | 97 | 3.1018 | 89.1 | 4.0464 | 99 | 4.0601 | 90.9 | 5.0908 | 101 | 5.108 | 94.5 | 7.3921 | 105 | 7.408 | 98.1 | 9.9129 | 109 | 9.9268 | 103.5 | 13.6417 | 115 | 13.658 | 112.5 | 20.0272 | 125 | 20.0413
81 | 0.40448 | 90 | 0.4184 | 82.8 | 0.86011 | 92 | 0.87467 | 86.4 | 2.182 | 96 | 2.1955 | 88.2 | 3.0245 | 98 | 3.0413 | 90 | 3.965 | 100 | 3.9788 | 91.8 | 4.9903 | 102 | 5.0038 | 95.4 | 7.2516 | 106 | 7.2663 | 99 | 9.7313 | 110 | 9.7455 | 104.4 | 13.4215 | 116 | 13.4351 | 113.4 | 19.7296 | 126 | 19.7434
81.9 | 0.39589 | 91 | 0.4101 | 83.7 | 0.84192 | 93 | 0.858 | 87.3 | 2.1368 | 97 | 2.1518 | 89.1 | 2.9631 | 99 | 2.9768 | 90.9 | 3.886 | 101 | 3.8997 | 92.7 | 4.8928 | 103 | 4.908 | 96.3 | 7.1151 | 107 | 7.1288 | 99.9 | 9.5546 | 111 | 9.5684 | 105.3 | 13.2067 | 117 | 13.2205 | 114.3 | 19.4384 | 127 | 19.4518
82.8 | 0.38751 | 92 | 0.4018 | 84.6 | 0.82431 | 94 | 0.84134 | 88.2 | 2.0931 | 98 | 2.108 | 90 | 2.9036 | 100 | 2.9184 | 91.8 | 3.8093 | 102 | 3.8247 | 93.6 | 4.7981 | 104 | 4.8122 | 97.2 | 6.9823 | 108 | 6.9997 | 100.8 | 9.3827 | 112 | 9.3997 | 106.2 | 12.9972 | 118 | 13.0101 | 115.2 | 19.154 | 128 | 19.1684
83.7 | 0.37942 | 93 | 0.3934 | 85.5 | 0.80723 | 95 | 0.8205 | 89.1 | 2.0506 | 99 | 2.0663 | 90.9 | 2.8458 | 101 | 2.8601 | 92.7 | 3.7349 | 103 | 3.7497 | 94.5 | 4.7061 | 105 | 4.7205 | 98.1 | 6.8533 | 109 | 6.8684 | 101.7 | 9.2153 | 113 | 9.2288 | 107.1 | 12.7928 | 119 | 12.808 | 116.1 | 18.8759 | 129 | 18.8913
84.6 | 0.3716 | 94 | 0.3851 | 86.4 | 0.79069 | 96 | 0.808 | 90 | 2.0095 | 100 | 2.0247 | 91.8 | 2.7897 | 102 | 2.8038 | 93.6 | 3.6627 | 104 | 3.6768 | 95.4 | 4.6168 | 106 | 4.633 | 99 | 6.7278 | 110 | 6.7413 | 102.6 | 9.0524 | 114 | 9.0663 | 108 | 12.5932 | 120 | 12.608 | 117 | 18.604 | 130 | 18.6184
85.5 | 0.36401 | 95 | 0.3768 | 87.3 | 0.77467 | 97 | 0.79134 | 90.9 | 1.97 | 101 | 1.9851 | 92.7 | 2.7352 | 103 | 2.7497 | 94.5 | 3.5925 | 105 | 3.608 | 96.3 | 4.5299 | 107 | 4.5434 | 99.9 | 6.6057 | 111 | 6.6184 | 103.5 | 8.8937 | 115 | 8.908 | 108.9 | 12.3984 | 121 | 12.4122 | 117.9 | 18.3379 | 131 | 18.3518
86.4 | 0.35665 | 96 | 0.3705 | 88.2 | 0.75913 | 98 | 0.77467 | 91.8 | 1.9318 | 102 | 1.9455 | 93.6 | 2.6824 | 104 | 2.6997 | 95.4 | 3.5243 | 106 | 3.5413 | 97.2 | 4.4455 | 108 | 4.4601 | 100.8 | 6.4869 | 112 | 6.5018 | 104.4 | 8.7391 | 116 | 8.7538 | 109.8 | 12.208 | 122 | 12.2247 | 118.8 | 18.0777 | 132 | 18.0913
87.3 | 0.34953 | 97 | 0.3663 | 89.1 | 0.74406 | 99 | 0.758 | 92.7 | 1.8946 | 103 | 1.908 | 94.5 | 2.631 | 105 | 2.6455 | 96.3 | 3.4581 | 107 | 3.4747 | 98.1 | 4.3634 | 109 | 4.3768 | 101.7 | 6.3712 | 113 | 6.3851 | 105.3 | 8.5886 | 117 | 8.6018 | 110.7 | 12.0223 | 123 | 12.0351 | 119.7 | 17.823 | 133 | 17.8372
88.2 | 0.32882 | 98 | 0.358 | 90 | 0.72943 | 100 | 0.74342 | 93.6 | 1.8585 | 104 | 1.8747 | 95.4 | 2.5812 | 106 | 2.5955 | 97.2 | 3.3937 | 108 | 3.408 | 99 | 4.2835 | 110 | 4.2997 | 102.6 | 6.2586 | 114 | 6.2747 | 106.2 | 8.4419 | 118 | 8.458 | 111.6 | 11.8408 | 124 | 11.858 | 120.6 | 17.574 | 134 | 17.5913
89.1 | 0.29501 | 99 | 0.3497 | 90.9 | 0.71524 | 101 | 0.72884 | 94.5 | 1.8235 | 105 | 1.8372 | 96.3 | 2.5327 | 107 | 2.5497 | 98.1 | 3.331 | 109 | 3.3455 | 99.9 | 4.2059 | 111 | 4.2205 | 103.5 | 6.149 | 115 | 6.1663 | 107.1 | 8.2988 | 119 | 8.3163 | 112.5 | 11.6634 | 125 | 11.6768 | 121.5 | 17.33 | 135 | 17.3434
90 | 0.047414 | 100 | 0.0623 | 91.8 | 0.70144 | 102 | 0.71634 | 95.4 | 1.7894 | 106 | 1.8038 | 97.2 | 2.4856 | 108 | 2.4997 | 99 | 3.2701 | 110 | 3.2851 | 100.8 | 4.1303 | 112 | 4.1434 | 104.4 | 6.0422 | 116 | 6.058 | 108 | 8.1595 | 120 | 8.1747 | 113.4 | 11.49 | 126 | 11.5038 | 122.4 | 17.0914 | 136 | 17.108
250.2 | 0.036109 | 500 | 0.05 | 92.7 | 0.68807 | 103 | 0.70175 | 96.3 | 1.7563 | 107 | 1.7705 | 98.1 | 2.4397 | 109 | 2.4538 | 99.9 | 3.2108 | 111 | 3.2247 | 101.7 | 4.0567 | 113 | 4.0705 | 105.3 | 5.9381 | 117 | 5.9518 | 108.9 | 8.0235 | 121 | 8.0372 | 114.3 | 11.3207 | 127 | 11.3351 | 123.3 | 16.8575 | 137 | 16.8747
250.2 | 0.0072687 | 500 | 0.033 | 93.6 | 0.67509 | 104 | 0.69134 | 97.2 | 1.7241 | 108 | 1.7413 | 99 | 2.3952 | 110 | 2.4101 | 100.8 | 3.1532 | 112 | 3.1684 | 102.6 | 3.9851 | 114 | 3.9997 | 106.2 | 5.8367 | 118 | 5.8518 | 109.8 | 7.8909 | 122 | 7.908 | 115.2 | 11.155 | 128 | 11.1684 | 124.2 | 16.6287 | 138 | 16.6434
468 | 0.003 | 1000 | 0.033 | 94.5 | 0.66247 | 105 | 0.67675 | 98.1 | 1.6928 | 109 | 1.708 | 99.9 | 2.3518 | 111 | 2.3663 | 101.7 | 3.0971 | 113 | 3.1101 | 103.5 | 3.9153 | 115 | 3.9288 | 107.1 | 5.7379 | 119 | 5.7518 | 110.7 | 7.7616 | 123 | 7.7768 | 116.1 | 10.9931 | 129 | 11.008 | 125.1 | 16.4046 | 139 | 16.4184
6300 | 0.003 | 6300 | 0.022 | 95.4 | 0.65021 | 106 | 0.66634 | 99 | 1.6623 | 110 | 1.6768 | 100.8 | 2.3096 | 112 | 2.3247 | 102.6 | 3.0424 | 114 | 3.058 | 104.4 | 3.8474 | 116 | 3.8601 | 108 | 5.6416 | 120 | 5.658 | 111.6 | 7.6354 | 124 | 7.6497 | 117 | 10.8348 | 130 | 10.8497 | 126 | 16.1851 | 140 | 16.1997
|  |  |  | 96.3 | 0.63829 | 107 | 0.65175 | 99.9 | 1.6327 | 111 | 1.6497 | 101.7 | 2.2686 | 113 | 2.283 | 103.5 | 2.9892 | 115 | 3.0038 | 105.3 | 3.7812 | 117 | 3.7955 | 108.9 | 5.5476 | 121 | 5.5622 | 112.5 | 7.5123 | 125 | 7.5268 | 117.9 | 10.6798 | 131 | 10.6934 | 126.9 | 15.97 | 141 | 15.9851
|  |  |  | 97.2 | 0.62669 | 108 | 0.64134 | 100.8 | 1.6038 | 112 | 1.6184 | 102.6 | 2.2286 | 114 | 2.2434 | 104.4 | 2.9373 | 116 | 2.9518 | 106.2 | 3.7167 | 118 | 3.733 | 109.8 | 5.456 | 122 | 5.4705 | 113.4 | 7.3921 | 126 | 7.408 | 118.8 | 10.5284 | 132 | 10.5434 | 127.8 | 15.7592 | 142 | 15.7747
|  |  |  | 98.1 | 0.61542 | 109 | 0.62884 | 101.7 | 1.5757 | 113 | 1.5913 | 103.5 | 2.1896 | 115 | 2.2038 | 105.3 | 2.8869 | 117 | 2.9018 | 107.1 | 3.6538 | 119 | 3.6684 | 110.7 | 5.3666 | 123 | 5.383 | 114.3 | 7.2747 | 127 | 7.2913 | 119.7 | 10.3801 | 133 | 10.3934 | 128.7 | 15.5529 | 143 | 15.5663
|  |  |  | 99 | 0.60445 | 110 | 0.61842 | 102.6 | 1.5484 | 114 | 1.5622 | 104.4 | 2.1517 | 116 | 2.1663 | 106.2 | 2.8376 | 118 | 2.8518 | 108 | 3.5925 | 120 | 3.608 | 111.6 | 5.2794 | 124 | 5.2934 | 115.2 | 7.1601 | 128 | 7.1747 | 120.6 | 10.2351 | 134 | 10.2497 | 129.6 | 15.3506 | 144 | 15.3663
|  |  |  | 99.9 | 0.59378 | 111 | 0.608 | 103.5 | 1.5217 | 115 | 1.5351 | 105.3 | 2.1148 | 117 | 2.1288 | 107.1 | 2.7897 | 119 | 2.8038 | 108.9 | 3.5327 | 121 | 3.5497 | 112.5 | 5.1943 | 125 | 5.208 | 116.1 | 7.0482 | 129 | 7.0622 | 121.5 | 10.0932 | 135 | 10.108 | 130.5 | 15.1521 | 145 | 15.1663
|  |  |  | 100.8 | 0.58339 | 112 | 0.59967 | 104.4 | 1.4958 | 116 | 1.5101 | 106.2 | 2.0787 | 118 | 2.0934 | 108 | 2.7429 | 120 | 2.758 | 109.8 | 3.4744 | 122 | 3.4913 | 113.4 | 5.1113 | 126 | 5.1247 | 117 | 6.9389 | 130 | 6.9518 | 122.4 | 9.9499 | 136 | 9.9663 | 131.4 | 14.9576 | 146 | 14.9747
|  |  |  | 101.7 | 0.57329 | 113 | 0.58717 | 105.3 | 1.4705 | 117 | 1.4851 | 107.1 | 2.0436 | 119 | 2.058 | 108.9 | 2.6973 | 121 | 2.7101 | 110.7 | 3.4176 | 123 | 3.433 | 114.3 | 5.0302 | 127 | 5.0434 | 117.9 | 6.8321 | 131 | 6.8497 | 123.3 | 9.8033 | 137 | 9.8184 | 132.3 | 14.767 | 147 | 14.783
|  |  |  | 102.6 | 0.56344 | 114 | 0.57675 | 106.2 | 1.4458 | 118 | 1.4601 | 108 | 2.0094 | 120 | 2.0247 | 109.8 | 2.6529 | 122 | 2.6663 | 111.6 | 3.3621 | 124 | 3.3768 | 115.2 | 4.951 | 128 | 4.9663 | 118.8 | 6.7278 | 132 | 6.7413 | 124.2 | 9.6601 | 138 | 9.6747 | 133.2 | 14.5801 | 148 | 14.5934
|  |  |  | 103.5 | 0.55383 | 115 | 0.56842 | 107.1 | 1.4217 | 119 | 1.4351 | 108.9 | 1.9765 | 121 | 1.9913 | 110.7 | 2.6095 | 123 | 2.6247 | 112.5 | 3.308 | 125 | 3.3247 | 116.1 | 4.8736 | 129 | 4.8872 | 119.7 | 6.6258 | 133 | 6.6413 | 125.1 | 9.5199 | 139 | 9.5351 | 134.1 | 14.3967 | 149 | 14.4101
|  |  |  | 104.4 | 0.54449 | 116 | 0.558 | 108 | 1.3983 | 120 | 1.4122 | 109.8 | 1.9444 | 122 | 1.958 | 111.6 | 2.5672 | 124 | 2.583 | 113.4 | 3.2551 | 126 | 3.2684 | 117 | 4.7981 | 130 | 4.8122 | 120.6 | 6.5261 | 134 | 6.5413 | 126 | 9.3826 | 140 | 9.3997 | 135 | 14.217 | 150 | 14.233
|  |  |  | 105.3 | 0.53538 | 117 | 0.54967 | 108.9 | 1.3754 | 121 | 1.3913 | 110.7 | 1.9131 | 123 | 1.9268 | 112.5 | 2.5259 | 125 | 2.5413 | 114.3 | 3.2035 | 127 | 3.2184 | 117.9 | 4.7243 | 131 | 4.7413 | 121.5 | 6.4286 | 135 | 6.4434 | 126.9 | 9.2484 | 141 | 9.2622 | 135.9 | 14.0406 | 151 | 14.0538
|  |  |  | 106.2 | 0.52649 | 118 | 0.54134 | 109.8 | 1.3531 | 122 | 1.3684 | 111.6 | 1.8825 | 124 | 1.8997 | 113.4 | 2.4855 | 126 | 2.4997 | 115.2 | 3.1532 | 128 | 3.1684 | 118.8 | 4.6522 | 132 | 4.6663 | 122.4 | 6.3333 | 136 | 6.3497 | 127.8 | 9.117 | 142 | 9.133 | 136.8 | 13.8675 | 152 | 13.883
|  |  |  | 107.1 | 0.51783 | 119 | 0.533 | 110.7 | 1.3314 | 123 | 1.3455 | 112.5 | 1.8526 | 125 | 1.8663 | 114.3 | 2.4462 | 127 | 2.4601 | 116.1 | 3.104 | 129 | 3.1184 | 119.7 | 4.5817 | 133 | 4.5955 | 123.3 | 6.2401 | 137 | 6.2538 | 128.7 | 8.9884 | 143 | 9.0018 | 137.7 | 13.6976 | 153 | 13.7122
|  |  |  | 108 | 0.5094 | 120 | 0.52467 | 111.6 | 1.3102 | 124 | 1.3247 | 113.4 | 1.8235 | 126 | 1.8372 | 115.2 | 2.4078 | 128 | 2.4247 | 117 | 3.0559 | 130 | 3.0705 | 120.6 | 4.5128 | 134 | 4.5268 | 124.2 | 6.1489 | 138 | 6.1663 | 129.6 | 8.8624 | 144 | 8.8768 | 138.6 | 13.5309 | 154 | 13.5455
|  |  |  | 108.9 | 0.50116 | 121 | 0.51634 | 112.5 | 1.2894 | 125 | 1.3038 | 114.3 | 1.795 | 127 | 1.8101 | 116.1 | 2.3702 | 129 | 2.3851 | 117.9 | 3.009 | 131 | 3.0247 | 121.5 | 4.4455 | 135 | 4.4601 | 125.1 | 6.0598 | 139 | 6.0747 | 130.5 | 8.7391 | 145 | 8.7518 | 139.5 | 13.3674 | 155 | 13.383
|  |  |  | 109.8 | 0.49312 | 122 | 0.508 | 113.4 | 1.2692 | 126 | 1.283 | 115.2 | 1.7672 | 128 | 1.783 | 117 | 2.3336 | 130 | 2.3497 | 118.8 | 2.9631 | 132 | 2.9768 | 122.4 | 4.3796 | 136 | 4.3934 | 126 | 5.9725 | 140 | 5.9872 | 131.4 | 8.6184 | 146 | 8.633 | 140.4 | 13.2067 | 156 | 13.2205
|  |  |  | 110.7 | 0.48531 | 123 | 0.49967 | 114.3 | 1.2494 | 127 | 1.2663 | 116.1 | 1.7401 | 129 | 1.7538 | 117.9 | 2.2977 | 131 | 2.3122 | 119.7 | 2.9183 | 133 | 2.933 | 123.3 | 4.3152 | 137 | 4.3288 | 126.9 | 5.8871 | 141 | 5.9018 | 132.3 | 8.5001 | 147 | 8.5163 | 141.3 | 13.0491 | 157 | 13.0663
|  |  |  | 111.6 | 0.47766 | 124 | 0.49134 | 115.2 | 1.2301 | 128 | 1.2434 | 117 | 1.7136 | 130 | 1.7268 | 118.8 | 2.2628 | 132 | 2.2768 | 120.6 | 2.8744 | 134 | 2.8913 | 124.2 | 4.2522 | 138 | 4.2663 | 127.8 | 5.8035 | 142 | 5.8184 | 133.2 | 8.3842 | 148 | 8.3997 | 142.2 | 12.8944 | 158 | 12.908
|  |  |  | 112.5 | 0.4702 | 125 | 0.48509 | 116.1 | 1.2113 | 129 | 1.2247 | 117.9 | 1.6876 | 131 | 1.7018 | 119.7 | 2.2286 | 133 | 2.2434 | 121.5 | 2.8316 | 135 | 2.8455 | 125.1 | 4.1906 | 139 | 4.208 | 128.7 | 5.7217 | 143 | 5.7351 | 134.1 | 8.2707 | 149 | 8.2851 | 143.1 | 12.7424 | 159 | 12.758
|  |  |  | 113.4 | 0.4629 | 126 | 0.47675 | 117 | 1.1928 | 130 | 1.208 | 118.8 | 1.6623 | 132 | 1.6768 | 120.6 | 2.1951 | 134 | 2.2101 | 122.4 | 2.7897 | 136 | 2.8038 | 126 | 4.1302 | 140 | 4.1434 | 129.6 | 5.6415 | 144 | 5.658 | 135 | 8.1595 | 150 | 8.1747 | 144 | 12.5932 | 160 | 12.608
|  |  |  | 114.3 | 0.45579 | 127 | 0.4705 | 117.9 | 1.1748 | 131 | 1.1913 | 119.7 | 1.6376 | 133 | 1.6518 | 121.5 | 2.1624 | 135 | 2.1768 | 123.3 | 2.7487 | 137 | 2.7622 | 126.9 | 4.0712 | 141 | 4.0851 | 130.5 | 5.5631 | 145 | 5.5768 | 135.9 | 8.0504 | 151 | 8.0663 | 144.9 | 12.4466 | 161 | 12.4601
|  |  |  | 115.2 | 0.44885 | 128 | 0.46217 | 118.8 | 1.1573 | 132 | 1.1747 | 120.6 | 1.6133 | 134 | 1.6268 | 122.4 | 2.1305 | 136 | 2.1434 | 124.2 | 2.7086 | 138 | 2.7247 | 127.8 | 4.0135 | 142 | 4.0268 | 131.4 | 5.4863 | 146 | 5.4997 | 136.8 | 7.9435 | 152 | 7.958 | 145.8 | 12.3026 | 162 | 12.3163
|  |  |  | 116.1 | 0.44206 | 129 | 0.458 | 119.7 | 1.1401 | 133 | 1.1538 | 121.5 | 1.5897 | 135 | 1.6038 | 123.3 | 2.0992 | 137 | 2.1163 | 125.1 | 2.6694 | 139 | 2.683 | 128.7 | 3.9569 | 143 | 3.9705 | 132.3 | 5.411 | 147 | 5.4247 | 137.7 | 7.8388 | 153 | 7.8518 | 146.7 | 12.1612 | 163 | 12.1747
|  |  |  | 117 | 0.43544 | 130 | 0.44967 | 120.6 | 1.1232 | 134 | 1.1372 | 122.4 | 1.5665 | 136 | 1.583 | 124.2 | 2.0686 | 138 | 2.083 | 126 | 2.631 | 140 | 2.6455 | 129.6 | 3.9015 | 144 | 3.9163 | 133.2 | 5.3373 | 148 | 5.3518 | 138.6 | 7.7361 | 154 | 7.7497 | 147.6 | 12.0223 | 164 | 12.0351
|  |  |  | 117.9 | 0.42895 | 131 | 0.44342 | 121.5 | 1.1068 | 135 | 1.1205 | 123.3 | 1.5439 | 137 | 1.558 | 125.1 | 2.0387 | 139 | 2.0518 | 126.9 | 2.5935 | 141 | 2.608 | 130.5 | 3.8473 | 145 | 3.8601 | 134.1 | 5.2651 | 149 | 5.2788 | 139.5 | 7.6354 | 155 | 7.6497 | 148.5 | 11.8856 | 165 | 11.8997
|  |  |  | 118.8 | 0.42262 | 132 | 0.43717 | 122.4 | 1.0907 | 136 | 1.108 | 124.2 | 1.5217 | 138 | 1.5351 | 126 | 2.0094 | 140 | 2.0247 | 127.8 | 2.5567 | 142 | 2.5705 | 131.4 | 3.7942 | 146 | 3.808 | 135 | 5.1943 | 150 | 5.208 | 140.4 | 7.5366 | 156 | 7.5518 | 149.4 | 11.7514 | 166 | 11.7663
|  |  |  | 119.7 | 0.41643 | 133 | 0.433 | 123.3 | 1.075 | 137 | 1.0913 | 125.1 | 1.5 | 139 | 1.5163 | 126.9 | 1.9812 | 141 | 1.9955 | 128.7 | 2.5208 | 143 | 2.5351 | 132.3 | 3.7422 | 147 | 3.758 | 135.9 | 5.1249 | 151 | 5.1413 | 141.3 | 7.4398 | 157 | 7.4538 | 150.3 | 11.6197 | 167 | 11.633
|  |  |  | 120.6 | 0.41037 | 134 | 0.42467 | 124.2 | 1.0596 | 138 | 1.0747 | 126 | 1.4788 | 140 | 1.4934 | 127.8 | 1.9535 | 142 | 1.9684 | 129.6 | 2.4855 | 144 | 2.4997 | 133.2 | 3.6913 | 148 | 3.708 | 136.8 | 5.057 | 152 | 5.0705 | 142.2 | 7.3448 | 158 | 7.3601 | 151.2 | 11.49 | 168 | 11.5038
|  |  |  | 121.5 | 0.40445 | 135 | 0.41842 | 125.1 | 1.0445 | 139 | 1.058 | 126.9 | 1.458 | 141 | 1.4747 | 128.7 | 1.9264 | 143 | 1.9413 | 130.5 | 2.451 | 145 | 2.4663 | 134.1 | 3.6414 | 149 | 3.658 | 137.7 | 4.9903 | 153 | 5.0038 | 143.1 | 7.2516 | 159 | 7.2663 | 152.1 | 11.3626 | 169 | 11.3768
|  |  |  | 122.4 | 0.39866 | 136 | 0.41217 | 126 | 1.0298 | 140 | 1.0434 | 127.8 | 1.4377 | 142 | 1.4518 | 129.6 | 1.8998 | 144 | 1.9163 | 131.4 | 2.4173 | 146 | 2.433 | 135 | 3.5925 | 150 | 3.608 | 138.6 | 4.925 | 154 | 4.9413 | 144 | 7.1601 | 160 | 7.1747 | 153 | 11.2373 | 170 | 11.2518
|  |  |  | 123.3 | 0.39299 | 137 | 0.408 | 126.9 | 1.0154 | 141 | 1.0288 | 128.7 | 1.4178 | 143 | 1.433 | 130.5 | 1.8739 | 145 | 1.8872 | 132.3 | 2.3842 | 147 | 2.3997 | 135.9 | 3.5446 | 151 | 3.558 | 139.5 | 4.8609 | 155 | 4.8747 | 144.9 | 7.0704 | 161 | 7.0851 | 153.9 | 11.1141 | 171 | 11.1288
|  |  |  | 124.2 | 0.38746 | 138 | 0.40175 | 127.8 | 1.0013 | 142 | 1.0163 | 129.6 | 1.3983 | 144 | 1.4122 | 131.4 | 1.8484 | 146 | 1.8622 | 133.2 | 2.3518 | 148 | 2.3663 | 136.8 | 3.4976 | 152 | 3.5122 | 140.4 | 4.7981 | 156 | 4.8122 | 145.8 | 6.9823 | 162 | 6.9997 | 154.8 | 10.9931 | 172 | 11.008
|  |  |  | 125.1 | 0.38203 | 139 | 0.3955 | 128.7 | 0.98744 | 143 | 1.0018 | 130.5 | 1.3792 | 145 | 1.3934 | 132.3 | 1.8235 | 147 | 1.8372 | 134.1 | 2.32 | 149 | 2.3351 | 137.7 | 3.4515 | 153 | 3.4663 | 141.3 | 4.7365 | 157 | 4.7518 | 146.7 | 6.8959 | 163 | 6.9101 | 155.7 | 10.874 | 173 | 10.8913
|  |  |  | 126 | 0.37672 | 140 | 0.39134 | 129.6 | 0.97389 | 144 | 0.99134 | 131.4 | 1.3605 | 146 | 1.3747 | 133.2 | 1.799 | 148 | 1.8163 | 135 | 2.2889 | 150 | 2.3018 | 138.6 | 3.4064 | 154 | 3.4205 | 142.2 | 4.676 | 158 | 4.6913 | 147.6 | 6.811 | 164 | 6.8247 | 156.6 | 10.7569 | 174 | 10.7705
|  |  |  | 126.9 | 0.37154 | 141 | 0.38509 | 130.5 | 0.96065 | 145 | 0.97467 | 132.3 | 1.3422 | 147 | 1.358 | 134.1 | 1.7751 | 149 | 1.7913 | 135.9 | 2.2584 | 151 | 2.2747 | 139.5 | 3.3621 | 155 | 3.3768 | 143.1 | 4.6167 | 159 | 4.633 | 148.5 | 6.7278 | 165 | 6.7413 | 157.5 | 10.6416 | 175 | 10.658
|  |  |  | 127.8 | 0.36644 | 142 | 0.383 | 131.4 | 0.94764 | 146 | 0.96217 | 133.2 | 1.3242 | 148 | 1.3413 | 135 | 1.7516 | 150 | 1.7663 | 136.8 | 2.2285 | 152 | 2.2434 | 140.4 | 3.3187 | 156 | 3.333 | 144 | 4.5586 | 160 | 4.5747 | 149.4 | 6.646 | 166 | 6.6601 | 158.4 | 10.5284 | 176 | 10.5434
|  |  |  | 128.7 | 0.36149 | 143 | 0.37675 | 132.3 | 0.93494 | 147 | 0.94967 | 134.1 | 1.3066 | 149 | 1.3205 | 135.9 | 1.7286 | 151 | 1.7434 | 137.7 | 2.1992 | 153 | 2.2163 | 141.3 | 3.2761 | 157 | 3.2913 | 144.9 | 4.5015 | 161 | 4.5163 | 150.3 | 6.5657 | 167 | 6.583 | 159.3 | 10.4169 | 177 | 10.433
|  |  |  | 129.6 | 0.35659 | 144 | 0.3705 | 133.2 | 0.92246 | 148 | 0.93717 | 135 | 1.2894 | 150 | 1.3038 | 136.8 | 1.7061 | 152 | 1.7205 | 138.6 | 2.1705 | 154 | 2.1851 | 142.2 | 3.2343 | 158 | 3.2497 | 145.8 | 4.4454 | 162 | 4.4601 | 151.2 | 6.4869 | 168 | 6.5018 | 160.2 | 10.3072 | 178 | 10.3247
|  |  |  | 130.5 | 0.35183 | 145 | 0.36634 | 134.1 | 0.91025 | 149 | 0.92467 | 135.9 | 1.2725 | 151 | 1.2872 | 137.7 | 1.684 | 153 | 1.6997 | 139.5 | 2.1423 | 155 | 2.158 | 143.1 | 3.1934 | 159 | 3.208 | 146.7 | 4.3904 | 163 | 4.408 | 152.1 | 6.4094 | 169 | 6.4247 | 161.1 | 10.1993 | 179 | 10.2163
|  |  |  | 131.4 | 0.34713 | 146 | 0.36009 | 135 | 0.89828 | 150 | 0.91217 | 136.8 | 1.2559 | 152 | 1.2705 | 138.6 | 1.6623 | 154 | 1.6768 | 140.4 | 2.1147 | 156 | 2.1288 | 144 | 3.1531 | 160 | 3.1684 | 147.6 | 4.3365 | 164 | 4.3518 | 153 | 6.3333 | 170 | 6.3497 | 162 | 10.0931 | 180 | 10.108
|  |  |  | 132.3 | 0.32878 | 147 | 0.358 | 135.9 | 0.88654 | 151 | 0.90175 | 137.7 | 1.2397 | 153 | 1.2538 | 139.5 | 1.641 | 155 | 1.658 | 141.3 | 2.0876 | 157 | 2.1018 | 144.9 | 3.1137 | 161 | 3.1268 | 148.5 | 4.2835 | 165 | 4.2997 | 153.9 | 6.2586 | 171 | 6.2747 | 162.9 | 9.987 | 181 | 10.0018
|  |  |  | 133.2 | 0.30148 | 148 | 0.35175 | 136.8 | 0.87504 | 152 | 0.89134 | 138.6 | 1.2238 | 154 | 1.2372 | 140.4 | 1.6202 | 156 | 1.6351 | 142.2 | 2.0611 | 158 | 2.0747 | 145.8 | 3.075 | 162 | 3.0913 | 149.4 | 4.2315 | 166 | 4.2455 | 154.8 | 6.1851 | 172 | 6.1997 | 163.8 | 9.8762 | 182 | 9.8913
|  |  |  | 134.1 | 0.28856 | 149 | 0.34967 | 137.7 | 0.86375 | 153 | 0.87675 | 139.5 | 1.2081 | 155 | 1.2247 | 141.3 | 1.5997 | 157 | 1.6163 | 143.1 | 2.035 | 159 | 2.0497 | 146.7 | 3.037 | 163 | 3.0518 | 150.3 | 4.1804 | 167 | 4.1934 | 155.7 | 6.113 | 173 | 6.1268 | 164.7 | 9.7672 | 183 | 9.783
|  |  |  | 135 | 0.047412 | 150 | 0.06231 | 138.6 | 0.8527 | 154 | 0.86634 | 140.4 | 1.1928 | 156 | 1.208 | 142.2 | 1.5797 | 158 | 1.5934 | 144 | 2.0094 | 160 | 2.0247 | 147.6 | 2.9997 | 164 | 3.0163 | 151.2 | 4.1302 | 168 | 4.1434 | 156.6 | 6.0421 | 174 | 6.058 | 165.6 | 9.66 | 184 | 9.6747
|  |  |  | 250.2 | 0.039364 | 500 | 0.05 | 139.5 | 0.84186 | 155 | 0.858 | 141.3 | 1.1778 | 157 | 1.1913 | 143.1 | 1.56 | 159 | 1.5747 | 144.9 | 1.9846 | 161 | 1.9997 | 148.5 | 2.9631 | 165 | 2.9768 | 152.1 | 4.081 | 169 | 4.0955 | 157.5 | 5.9724 | 175 | 5.9872 | 166.5 | 9.5546 | 185 | 9.5684
|  |  |  | 250.2 | 0.0072687 | 500 | 0.033 | 140.4 | 0.8312 | 156 | 0.8455 | 142.2 | 1.1631 | 158 | 1.1768 | 144 | 1.5406 | 160 | 1.558 | 145.8 | 1.9603 | 162 | 1.9747 | 149.4 | 2.9271 | 166 | 2.9413 | 153 | 4.0326 | 170 | 4.0497 | 158.4 | 5.904 | 176 | 5.9184 | 167.4 | 9.4509 | 186 | 9.4663
|  |  |  | 468 | 0.003 | 1000 | 0.033 | 141.3 | 0.82077 | 157 | 0.83509 | 143.1 | 1.1486 | 159 | 1.1622 | 144.9 | 1.5217 | 161 | 1.5351 | 146.7 | 1.9365 | 163 | 1.9518 | 150.3 | 2.8918 | 167 | 2.908 | 153.9 | 3.985 | 171 | 3.9997 | 159.3 | 5.8367 | 177 | 5.8518 | 168.3 | 9.3488 | 187 | 9.3663
|  |  |  | 6300 | 0.003 | 6300 | 0.022 | 142.2 | 0.81054 | 158 | 0.82467 | 144 | 1.1344 | 160 | 1.1497 | 145.8 | 1.5031 | 162 | 1.5163 | 147.6 | 1.913 | 164 | 1.9268 | 151.2 | 2.8572 | 168 | 2.8705 | 154.8 | 3.9383 | 172 | 3.9518 | 160.2 | 5.7705 | 178 | 5.7851 | 169.2 | 9.2484 | 188 | 9.2622
[8 empty] | 143.1 | 0.8005 | 159 | 0.81634 | 144.9 | 1.1205 | 161 | 1.1351 | 146.7 | 1.4848 | 163 | 1.4997 | 148.5 | 1.89 | 165 | 1.9038 | 152.1 | 2.8231 | 169 | 2.8372 | 155.7 | 3.8924 | 173 | 3.908 | 161.1 | 5.7055 | 179 | 5.7184 | 170.1 | 9.1496 | 189 | 9.1663
[8 empty] | 144 | 0.79063 | 160 | 0.808 | 145.8 | 1.1068 | 162 | 1.1205 | 147.6 | 1.4669 | 164 | 1.483 | 149.4 | 1.8674 | 166 | 1.883 | 153 | 2.7897 | 170 | 2.8038 | 156.6 | 3.8473 | 174 | 3.8601 | 162 | 5.6415 | 180 | 5.658 | 171 | 9.0523 | 190 | 9.0663
[8 empty] | 144.9 | 0.78095 | 161 | 0.7955 | 146.7 | 1.0934 | 163 | 1.108 | 148.5 | 1.4492 | 165 | 1.4663 | 150.3 | 1.8453 | 167 | 1.8601 | 153.9 | 2.7568 | 171 | 2.7705 | 157.5 | 3.803 | 175 | 3.8163 | 162.9 | 5.5786 | 181 | 5.5934 | 171.9 | 8.9566 | 191 | 8.9705
[8 empty] | 145.8 | 0.77145 | 162 | 0.78509 | 147.6 | 1.0802 | 164 | 1.0934 | 149.4 | 1.432 | 166 | 1.4455 | 151.2 | 1.8235 | 168 | 1.8372 | 154.8 | 2.7245 | 172 | 2.7413 | 158.4 | 3.7594 | 176 | 3.7747 | 163.8 | 5.5168 | 182 | 5.533 | 172.8 | 8.8624 | 192 | 8.8768
[8 empty] | 146.7 | 0.76213 | 163 | 0.77675 | 148.5 | 1.0672 | 165 | 1.083 | 150.3 | 1.415 | 167 | 1.4288 | 152.1 | 1.8021 | 169 | 1.8163 | 155.7 | 2.6928 | 173 | 2.708 | 159.3 | 3.7166 | 177 | 3.733 | 164.7 | 5.456 | 183 | 5.4705 | 173.7 | 8.7697 | 193 | 8.783
[8 empty] | 147.6 | 0.75297 | 164 | 0.76634 | 149.4 | 1.0545 | 166 | 1.0684 | 151.2 | 1.3983 | 168 | 1.4122 | 153 | 1.781 | 170 | 1.7955 | 156.6 | 2.6616 | 174 | 2.6768 | 160.2 | 3.6745 | 178 | 3.6913 | 165.6 | 5.3961 | 184 | 5.4101 | 174.6 | 8.6784 | 194 | 8.6934
[8 empty] | 148.5 | 0.744 | 165 | 0.758 | 150.3 | 1.0421 | 167 | 1.058 | 152.1 | 1.3819 | 169 | 1.3955 | 153.9 | 1.7604 | 171 | 1.7747 | 157.5 | 2.631 | 175 | 2.6455 | 161.1 | 3.6332 | 179 | 3.6497 | 166.5 | 5.3373 | 185 | 5.3518 | 175.5 | 8.5886 | 195 | 8.6018
[8 empty] | 149.4 | 0.73518 | 166 | 0.74967 | 151.2 | 1.0298 | 168 | 1.0434 | 153 | 1.3658 | 170 | 1.383 | 154.8 | 1.7401 | 172 | 1.7538 | 158.4 | 2.6009 | 176 | 2.6163 | 162 | 3.5925 | 180 | 3.608 | 167.4 | 5.2794 | 186 | 5.2934 | 176.4 | 8.5001 | 196 | 8.5163
[8 empty] | 150.3 | 0.72652 | 167 | 0.74134 | 152.1 | 1.0178 | 169 | 1.033 | 153.9 | 1.35 | 171 | 1.3663 | 155.7 | 1.7201 | 173 | 1.7351 | 159.3 | 2.5713 | 177 | 2.5851 | 162.9 | 3.5525 | 181 | 3.5663 | 168.3 | 5.2224 | 187 | 5.2372 | 177.3 | 8.413 | 197 | 8.4268
[8 empty] | 151.2 | 0.71801 | 168 | 0.733 | 153 | 1.0059 | 170 | 1.0205 | 154.8 | 1.3344 | 172 | 1.3497 | 156.6 | 1.7005 | 174 | 1.7163 | 160.2 | 2.5422 | 178 | 2.558 | 163.8 | 3.5131 | 182 | 3.5268 | 169.2 | 5.1664 | 188 | 5.183 | 178.2 | 8.3272 | 198 | 8.3413
[8 empty] | 152.1 | 0.70964 | 169 | 0.72467 | 153.9 | 0.99431 | 171 | 1.008 | 155.7 | 1.3192 | 173 | 1.333 | 157.5 | 1.6812 | 175 | 1.6955 | 161.1 | 2.5136 | 179 | 2.5268 | 164.7 | 3.4744 | 183 | 3.4913 | 170.1 | 5.1112 | 189 | 5.1247 | 179.1 | 8.2426 | 199 | 8.258
[8 empty] | 153 | 0.70143 | 170 | 0.71634 | 154.8 | 0.98289 | 172 | 0.99967 | 156.6 | 1.3041 | 174 | 1.3184 | 158.4 | 1.6623 | 176 | 1.6768 | 162 | 2.4855 | 180 | 2.4997 | 165.6 | 3.4364 | 184 | 3.4497 | 171 | 5.0569 | 190 | 5.0705 | 180 | 8.1594 | 200 | 8.1747
[8 empty] | 153.9 | 0.69335 | 171 | 0.708 | 155.7 | 0.97166 | 173 | 0.98509 | 157.5 | 1.2894 | 175 | 1.3038 | 159.3 | 1.6437 | 177 | 1.658 | 162.9 | 2.4579 | 181 | 2.4747 | 166.5 | 3.3989 | 185 | 3.4163 | 171.9 | 5.0035 | 191 | 5.0184 | 180.9 | 8.0775 | 201 | 8.0913
[8 empty] | 154.8 | 0.68542 | 172 | 0.69967 | 156.6 | 0.96063 | 174 | 0.97467 | 158.4 | 1.2749 | 176 | 1.2913 | 160.2 | 1.6254 | 178 | 1.6413 | 163.8 | 2.4307 | 182 | 2.4434 | 167.4 | 3.3621 | 186 | 3.3768 | 172.8 | 4.9509 | 192 | 4.9663 | 181.8 | 7.9967 | 202 | 8.0101
[8 empty] | 155.7 | 0.67763 | 173 | 0.69134 | 157.5 | 0.94978 | 175 | 0.96634 | 159.3 | 1.2606 | 177 | 1.2747 | 161.1 | 1.6073 | 179 | 1.6247 | 164.7 | 2.404 | 183 | 2.4184 | 168.3 | 3.3258 | 187 | 3.3413 | 173.7 | 4.8992 | 193 | 4.9163 | 182.7 | 7.9172 | 203 | 7.933
[8 empty] | 156.6 | 0.66996 | 174 | 0.68509 | 158.4 | 0.93913 | 176 | 0.95384 | 160.2 | 1.2466 | 178 | 1.2601 | 162 | 1.5896 | 180 | 1.6038 | 165.6 | 2.3776 | 184 | 2.3913 | 169.2 | 3.2902 | 188 | 3.3038 | 174.6 | 4.8482 | 194 | 4.8622 | 183.6 | 7.8388 | 204 | 7.8518
[8 empty] | 157.5 | 0.66243 | 175 | 0.67675 | 159.3 | 0.92866 | 177 | 0.94342 | 161.1 | 1.2328 | 179 | 1.2497 | 162.9 | 1.5722 | 181 | 1.5851 | 166.5 | 2.3518 | 185 | 2.3663 | 170.1 | 3.2551 | 189 | 3.2684 | 175.5 | 4.7981 | 195 | 4.8122 | 184.5 | 7.7616 | 205 | 7.7768
[8 empty] | 158.4 | 0.65503 | 176 | 0.66842 | 160.2 | 0.91836 | 178 | 0.933 | 162 | 1.2193 | 180 | 1.233 | 163.8 | 1.5551 | 182 | 1.5684 | 167.4 | 2.3263 | 186 | 2.3413 | 171 | 3.2206 | 190 | 3.2351 | 176.4 | 4.7487 | 196 | 4.7622 | 185.4 | 7.6855 | 206 | 7.6997
[8 empty] | 159.3 | 0.64776 | 177 | 0.66217 | 161.1 | 0.90822 | 179 | 0.92467 | 162.9 | 1.2059 | 181 | 1.2205 | 164.7 | 1.5383 | 183 | 1.5518 | 168.3 | 2.3013 | 187 | 2.3163 | 171.9 | 3.1866 | 191 | 3.2018 | 177.3 | 4.7001 | 197 | 4.7163 | 186.3 | 7.6105 | 207 | 7.6247
[8 empty] | 160.2 | 0.6406 | 178 | 0.658 | 162 | 0.89827 | 180 | 0.91217 | 163.8 | 1.1928 | 182 | 1.208 | 165.6 | 1.5217 | 184 | 1.5351 | 169.2 | 2.2766 | 188 | 2.2913 | 172.8 | 3.1531 | 192 | 3.1684 | 178.2 | 4.6522 | 198 | 4.6663 | 187.2 | 7.5366 | 208 | 7.5518
[8 empty] | 161.1 | 0.63357 | 179 | 0.64967 | 162.9 | 0.88846 | 181 | 0.90175 | 164.7 | 1.1799 | 183 | 1.1934 | 166.5 | 1.5054 | 185 | 1.5184 | 170.1 | 2.2524 | 189 | 2.2663 | 173.7 | 3.1202 | 193 | 3.1351 | 179.1 | 4.605 | 199 | 4.6184 | 188.1 | 7.4638 | 209 | 7.4768
[8 empty] | 162 | 0.62665 | 180 | 0.64134 | 163.8 | 0.87885 | 182 | 0.89342 | 165.6 | 1.1672 | 184 | 1.183 | 167.4 | 1.4893 | 186 | 1.5038 | 171 | 2.2285 | 190 | 2.2434 | 174.6 | 3.0878 | 194 | 3.1018 | 180 | 4.5586 | 200 | 4.5747 | 189 | 7.392 | 210 | 7.408
[8 empty] | 162.9 | 0.61984 | 181 | 0.63509 | 164.7 | 0.86937 | 183 | 0.883 | 166.5 | 1.1547 | 185 | 1.1684 | 168.3 | 1.4735 | 187 | 1.4872 | 171.9 | 2.205 | 191 | 2.2184 | 175.5 | 3.0559 | 195 | 3.0705 | 180.9 | 4.5128 | 201 | 4.5268 | 189.9 | 7.3213 | 211 | 7.3351
[8 empty] | 163.8 | 0.61317 | 182 | 0.62675 | 165.6 | 0.86004 | 184 | 0.87467 | 167.4 | 1.1425 | 186 | 1.158 | 169.2 | 1.458 | 188 | 1.4747 | 172.8 | 2.1819 | 192 | 2.1955 | 176.4 | 3.0245 | 196 | 3.0413 | 181.8 | 4.4677 | 202 | 4.483 | 190.8 | 7.2515 | 212 | 7.2663
[8 empty] | 164.7 | 0.60659 | 183 | 0.6205 | 166.5 | 0.85087 | 185 | 0.86634 | 168.3 | 1.1304 | 187 | 1.1434 | 170.1 | 1.4427 | 189 | 1.458 | 173.7 | 2.1592 | 193 | 2.1747 | 177.3 | 2.9935 | 197 | 3.008 | 182.7 | 4.4233 | 203 | 4.4372 | 191.7 | 7.1828 | 213 | 7.1997
[8 empty] | 165.6 | 0.60011 | 184 | 0.61634 | 167.4 | 0.84185 | 186 | 0.858 | 169.2 | 1.1185 | 188 | 1.133 | 171 | 1.4277 | 190 | 1.4413 | 174.6 | 2.1368 | 194 | 2.1518 | 178.2 | 2.9631 | 198 | 2.9768 | 183.6 | 4.3796 | 204 | 4.3934 | 192.6 | 7.115 | 214 | 7.1288
[8 empty] | 166.5 | 0.59374 | 185 | 0.608 | 168.3 | 0.83296 | 187 | 0.84967 | 170.1 | 1.1068 | 189 | 1.1205 | 171.9 | 1.4129 | 191 | 1.4268 | 175.5 | 2.1147 | 195 | 2.1288 | 179.1 | 2.9331 | 199 | 2.9497 | 184.5 | 4.3365 | 205 | 4.3518 | 193.5 | 7.0482 | 215 | 7.0622
[8 empty] | 167.4 | 0.58747 | 186 | 0.60175 | 169.2 | 0.82423 | 188 | 0.84134 | 171 | 1.0953 | 190 | 1.1101 | 172.8 | 1.3983 | 192 | 1.4122 | 176.4 | 2.093 | 196 | 2.108 | 180 | 2.9035 | 200 | 2.9184 | 185.4 | 4.294 | 206 | 4.308 | 194.4 | 6.9823 | 216 | 6.9997
[8 empty] | 168.3 | 0.5813 | 187 | 0.5955 | 170.1 | 0.81563 | 189 | 0.833 | 171.9 | 1.0839 | 191 | 1.0997 | 173.7 | 1.3839 | 193 | 1.3997 | 177.3 | 2.0716 | 197 | 2.0851 | 180.9 | 2.8744 | 201 | 2.8913 | 186.3 | 4.2522 | 207 | 4.2663 | 195.3 | 6.9173 | 217 | 6.933
[8 empty] | 169.2 | 0.57524 | 188 | 0.59134 | 171 | 0.80715 | 190 | 0.8205 | 172.8 | 1.0727 | 192 | 1.0872 | 174.6 | 1.3698 | 194 | 1.3851 | 178.2 | 2.0506 | 198 | 2.0663 | 181.8 | 2.8457 | 202 | 2.8601 | 187.2 | 4.2109 | 208 | 4.2247 | 196.2 | 6.8532 | 218 | 6.8684
[8 empty] | 170.1 | 0.56927 | 189 | 0.583 | 171.9 | 0.79882 | 191 | 0.81217 | 173.7 | 1.0618 | 193 | 1.0768 | 175.5 | 1.3559 | 195 | 1.3705 | 179.1 | 2.0298 | 199 | 2.0434 | 182.7 | 2.8175 | 203 | 2.833 | 188.1 | 4.1703 | 209 | 4.1851 | 197.1 | 6.79 | 219 | 6.8038
[8 empty] | 171 | 0.56339 | 190 | 0.57675 | 172.8 | 0.79062 | 192 | 0.808 | 174.6 | 1.0509 | 194 | 1.0663 | 176.4 | 1.3422 | 196 | 1.358 | 180 | 2.0094 | 200 | 2.0247 | 183.6 | 2.7896 | 204 | 2.8038 | 189 | 4.1302 | 210 | 4.1434 | 198 | 6.7277 | 220 | 6.7413
[8 empty] | 171.9 | 0.5576 | 191 | 0.57467 | 173.7 | 0.78255 | 193 | 0.79967 | 175.5 | 1.0403 | 195 | 1.0538 | 177.3 | 1.3287 | 197 | 1.3434 | 180.9 | 1.9896 | 201 | 2.0038 | 184.5 | 2.7622 | 205 | 2.7768 | 189.9 | 4.0907 | 211 | 4.108 | 198.9 | 6.6663 | 221 | 6.683
[8 empty] | 172.8 | 0.55189 | 192 | 0.56634 | 174.6 | 0.77459 | 194 | 0.79134 | 176.4 | 1.0298 | 196 | 1.0434 | 178.2 | 1.3154 | 198 | 1.3288 | 181.8 | 1.97 | 202 | 1.9851 | 185.4 | 2.7352 | 206 | 2.7497 | 190.8 | 4.0518 | 212 | 4.0663 | 199.8 | 6.6056 | 222 | 6.6184
[8 empty] | 173.7 | 0.5463 | 193 | 0.56009 | 175.5 | 0.76678 | 195 | 0.783 | 177.3 | 1.0195 | 197 | 1.033 | 179.1 | 1.3023 | 199 | 1.3163 | 182.7 | 1.9507 | 203 | 1.9663 | 186.3 | 2.7086 | 207 | 2.7247 | 191.7 | 4.0134 | 213 | 4.0268 | 200.7 | 6.5458 | 223 | 6.5601
[8 empty] | 174.6 | 0.54077 | 194 | 0.558 | 176.4 | 0.75905 | 196 | 0.77467 | 178.2 | 1.0093 | 198 | 1.0247 | 180 | 1.2894 | 200 | 1.3038 | 183.6 | 1.9317 | 204 | 1.9455 | 187.2 | 2.6824 | 208 | 2.6997 | 192.6 | 3.9756 | 214 | 3.9913 | 201.6 | 6.4868 | 224 | 6.5018
[8 empty] | 175.5 | 0.53534 | 195 | 0.54967 | 177.3 | 0.75148 | 197 | 0.76634 | 179.1 | 0.99924 | 199 | 1.0163 | 180.9 | 1.2767 | 201 | 1.2913 | 184.5 | 1.913 | 205 | 1.9268 | 188.1 | 2.6565 | 209 | 2.6705 | 193.5 | 3.9383 | 215 | 3.9518 | 202.5 | 6.4286 | 225 | 6.4434
[8 empty] | 176.4 | 0.52998 | 196 | 0.54342 | 178.2 | 0.74398 | 198 | 0.758 | 180 | 0.98937 | 200 | 1.0038 | 181.8 | 1.2642 | 202 | 1.2788 | 185.4 | 1.8946 | 206 | 1.908 | 189 | 2.631 | 210 | 2.6455 | 194.4 | 3.9015 | 216 | 3.9163 | 203.4 | 6.3712 | 226 | 6.3851
[8 empty] | 177.3 | 0.52471 | 197 | 0.54134 | 179.1 | 0.73661 | 199 | 0.75175 | 180.9 | 0.97965 | 201 | 0.99342 | 182.7 | 1.2518 | 203 | 1.2663 | 186.3 | 1.8764 | 207 | 1.8913 | 189.9 | 2.6059 | 211 | 2.6205 | 195.3 | 3.8653 | 217 | 3.8788 | 204.3 | 6.3145 | 227 | 6.3288
[8 empty] | 178.2 | 0.51951 | 198 | 0.533 | 180 | 0.72936 | 200 | 0.74342 | 181.8 | 0.97007 | 202 | 0.98509 | 183.6 | 1.2397 | 204 | 1.2538 | 187.2 | 1.8585 | 208 | 1.8747 | 190.8 | 2.5811 | 212 | 2.5955 | 196.2 | 3.8295 | 218 | 3.8434 | 205.2 | 6.2586 | 228 | 6.2747
[8 empty] | 179.1 | 0.5144 | 199 | 0.52884 | 180.9 | 0.72223 | 201 | 0.73509 | 182.7 | 0.96063 | 203 | 0.97467 | 184.5 | 1.2277 | 205 | 1.2413 | 188.1 | 1.8409 | 209 | 1.858 | 191.7 | 2.5567 | 213 | 2.5705 | 197.1 | 3.7942 | 219 | 3.808 | 206.1 | 6.2034 | 229 | 6.2184
[8 empty] | 180 | 0.50936 | 200 | 0.52467 | 181.8 | 0.71518 | 202 | 0.72884 | 183.6 | 0.95132 | 204 | 0.96634 | 185.4 | 1.2159 | 206 | 1.233 | 189 | 1.8234 | 210 | 1.8372 | 192.6 | 2.5326 | 214 | 2.5497 | 198 | 3.7594 | 220 | 3.7747 | 207 | 6.1489 | 230 | 6.1663
[8 empty] | 180.9 | 0.50441 | 201 | 0.51842 | 182.7 | 0.70826 | 203 | 0.72467 | 184.5 | 0.94216 | 205 | 0.958 | 186.3 | 1.2043 | 207 | 1.2184 | 189.9 | 1.8063 | 211 | 1.8205 | 193.5 | 2.5089 | 215 | 2.5247 | 198.9 | 3.7251 | 221 | 3.7413 | 207.9 | 6.0952 | 231 | 6.1101
[8 empty] | 181.8 | 0.49952 | 202 | 0.51634 | 183.6 | 0.70141 | 204 | 0.71634 | 185.4 | 0.9331 | 206 | 0.94967 | 187.2 | 1.1928 | 208 | 1.208 | 190.8 | 1.7894 | 212 | 1.8038 | 194.4 | 2.4855 | 216 | 2.4997 | 199.8 | 3.6913 | 222 | 3.708 | 208.8 | 6.0421 | 232 | 6.058
[8 empty] | 182.7 | 0.4947 | 203 | 0.508 | 184.5 | 0.69468 | 205 | 0.708 | 186.3 | 0.92422 | 207 | 0.94134 | 188.1 | 1.1815 | 209 | 1.1955 | 191.7 | 1.7727 | 213 | 1.7872 | 195.3 | 2.4624 | 217 | 2.4768 | 200.7 | 3.6579 | 223 | 3.6747 | 209.7 | 5.9897 | 233 | 6.0038
[8 empty] | 183.6 | 0.48994 | 204 | 0.50384 | 185.4 | 0.68802 | 206 | 0.70175 | 187.2 | 0.91544 | 208 | 0.92884 | 189 | 1.1704 | 210 | 1.1851 | 192.6 | 1.7563 | 214 | 1.7705 | 196.2 | 2.4397 | 218 | 2.4538 | 201.6 | 3.6249 | 224 | 3.6413 | 210.6 | 5.9381 | 234 | 5.9518
[8 empty] | 184.5 | 0.48528 | 205 | 0.49967 | 186.3 | 0.6815 | 207 | 0.6955 | 188.1 | 0.90679 | 209 | 0.9205 | 189.9 | 1.1594 | 211 | 1.1747 | 193.5 | 1.7401 | 215 | 1.7538 | 197.1 | 2.4172 | 219 | 2.433 | 202.5 | 3.5925 | 225 | 3.608 | 211.5 | 5.887 | 235 | 5.9018
[8 empty] | 185.4 | 0.48065 | 206 | 0.49342 | 187.2 | 0.67504 | 208 | 0.69134 | 189 | 0.89825 | 210 | 0.91217 | 190.8 | 1.1486 | 212 | 1.1622 | 194.4 | 1.7241 | 216 | 1.7413 | 198 | 2.3951 | 220 | 2.4101 | 203.4 | 3.5604 | 226 | 3.5747 | 212.4 | 5.8367 | 236 | 5.8518
[8 empty] | 186.3 | 0.47613 | 207 | 0.49134 | 188.1 | 0.66869 | 209 | 0.683 | 189.9 | 0.88985 | 211 | 0.90384 | 191.7 | 1.1379 | 213 | 1.1518 | 195.3 | 1.7083 | 217 | 1.7247 | 198.9 | 2.3733 | 221 | 2.3872 | 204.3 | 3.5288 | 227 | 3.5434 | 213.3 | 5.7869 | 237 | 5.8018
[8 empty] | 187.2 | 0.47164 | 208 | 0.48509 | 189 | 0.66242 | 210 | 0.67675 | 190.8 | 0.88157 | 212 | 0.8955 | 192.6 | 1.1274 | 214 | 1.1413 | 196.2 | 1.6927 | 218 | 1.708 | 199.8 | 2.3518 | 222 | 2.3663 | 205.2 | 3.4976 | 228 | 3.5122 | 214.2 | 5.7378 | 238 | 5.7518
[8 empty] | 188.1 | 0.46722 | 209 | 0.483 | 189.9 | 0.65625 | 211 | 0.6705 | 191.7 | 0.87341 | 213 | 0.88717 | 193.5 | 1.117 | 215 | 1.133 | 197.1 | 1.6774 | 219 | 1.6913 | 200.7 | 2.3305 | 223 | 2.3434 | 206.1 | 3.4667 | 229 | 3.483 | 215.1 | 5.6894 | 239 | 5.7038
[8 empty] | 189 | 0.46286 | 210 | 0.47675 | 190.8 | 0.65017 | 212 | 0.66634 | 192.6 | 0.86533 | 214 | 0.87884 | 194.4 | 1.1068 | 216 | 1.1205 | 198 | 1.6623 | 220 | 1.6768 | 201.6 | 2.3096 | 224 | 2.3247 | 207 | 3.4363 | 230 | 3.4497 | 216 | 5.6415 | 240 | 5.658
[8 empty] | 189.9 | 0.45859 | 211 | 0.47467 | 191.7 | 0.64416 | 213 | 0.658 | 193.5 | 0.8574 | 215 | 0.87467 | 195.3 | 1.0967 | 217 | 1.1101 | 198.9 | 1.6474 | 221 | 1.6601 | 202.5 | 2.2889 | 225 | 2.3018 | 207.9 | 3.4063 | 231 | 3.4205 | 216.9 | 5.5942 | 241 | 5.608
[8 empty] | 190.8 | 0.45436 | 212 | 0.46842 | 192.6 | 0.63824 | 214 | 0.65175 | 194.4 | 0.84955 | 216 | 0.86634 | 196.2 | 1.0867 | 218 | 1.1018 | 199.8 | 1.6326 | 222 | 1.6497 | 203.4 | 2.2685 | 226 | 2.283 | 208.8 | 3.3767 | 232 | 3.3913 | 217.8 | 5.5476 | 242 | 5.5622
[8 empty] | 191.7 | 0.4502 | 213 | 0.46634 | 193.5 | 0.6324 | 215 | 0.64967 | 195.3 | 0.84183 | 217 | 0.858 | 197.1 | 1.0769 | 219 | 1.0913 | 200.7 | 1.6181 | 223 | 1.633 | 204.3 | 2.2484 | 227 | 2.2622 | 209.7 | 3.3475 | 233 | 3.3622 | 218.7 | 5.5015 | 243 | 5.5163
[8 empty] | 192.6 | 0.44607 | 214 | 0.46009 | 194.4 | 0.62663 | 216 | 0.64134 | 196.2 | 0.83421 | 218 | 0.84967 | 198 | 1.0672 | 220 | 1.083 | 201.6 | 1.6038 | 224 | 1.6184 | 205.2 | 2.2285 | 228 | 2.2434 | 210.6 | 3.3186 | 234 | 3.333 | 219.6 | 5.4559 | 244 | 5.4705
[8 empty] | 193.5 | 0.44202 | 215 | 0.458 | 195.3 | 0.62096 | 217 | 0.63509 | 197.1 | 0.82668 | 219 | 0.84134 | 198.9 | 1.0577 | 221 | 1.0747 | 202.5 | 1.5896 | 225 | 1.6038 | 206.1 | 2.2089 | 229 | 2.2247 | 211.5 | 3.2902 | 235 | 3.3038 | 220.5 | 5.411 | 245 | 5.4247
[8 empty] | 194.4 | 0.43802 | 216 | 0.45175 | 196.2 | 0.61536 | 218 | 0.62884 | 198 | 0.81928 | 220 | 0.833 | 199.8 | 1.0482 | 222 | 1.0622 | 203.4 | 1.5757 | 226 | 1.5913 | 207 | 2.1896 | 230 | 2.2038 | 212.4 | 3.2621 | 236 | 3.2768 | 221.4 | 5.3666 | 246 | 5.383
[8 empty] | 195.3 | 0.43408 | 217 | 0.44967 | 197.1 | 0.60984 | 219 | 0.62467 | 198.9 | 0.81196 | 221 | 0.82675 | 200.7 | 1.0389 | 223 | 1.0518 | 204.3 | 1.5619 | 227 | 1.5768 | 207.9 | 2.1705 | 231 | 2.1851 | 213.3 | 3.2343 | 237 | 3.2497 | 222.3 | 5.3227 | 247 | 5.3372
[8 empty] | 196.2 | 0.43019 | 218 | 0.44342 | 198 | 0.6044 | 220 | 0.61842 | 199.8 | 0.80475 | 222 | 0.81842 | 201.6 | 1.0298 | 224 | 1.0434 | 205.2 | 1.5483 | 228 | 1.5622 | 208.8 | 2.1517 | 232 | 2.1663 | 214.2 | 3.2069 | 238 | 3.2205 | 223.2 | 5.2794 | 248 | 5.2934
[8 empty] | 197.1 | 0.42635 | 219 | 0.44134 | 198.9 | 0.59903 | 221 | 0.61634 | 200.7 | 0.79762 | 223 | 0.81217 | 202.5 | 1.0207 | 225 | 1.0351 | 206.1 | 1.5349 | 229 | 1.5497 | 209.7 | 2.133 | 233 | 2.1497 | 215.1 | 3.1798 | 239 | 3.1934 | 224.1 | 5.2365 | 249 | 5.2518
[8 empty] | 198 | 0.42257 | 220 | 0.43717 | 199.8 | 0.59372 | 222 | 0.608 | 201.6 | 0.7906 | 224 | 0.808 | 203.4 | 1.0118 | 226 | 1.0268 | 207 | 1.5217 | 230 | 1.5351 | 210.6 | 2.1147 | 234 | 2.1288 | 216 | 3.1531 | 240 | 3.1684 | 225 | 5.1943 | 250 | 5.208
[8 empty] | 198.9 | 0.41884 | 221 | 0.433 | 200.7 | 0.58849 | 223 | 0.60175 | 202.5 | 0.78368 | 225 | 0.79967 | 204.3 | 1.003 | 227 | 1.0163 | 207.9 | 1.5086 | 231 | 1.5247 | 211.5 | 2.0966 | 235 | 2.1101 | 216.9 | 3.1267 | 241 | 3.1413 | 225.9 | 5.1525 | 251 | 5.1663
[8 empty] | 199.8 | 0.41516 | 222 | 0.42884 | 201.6 | 0.58333 | 224 | 0.59967 | 203.4 | 0.77684 | 226 | 0.79134 | 205.2 | 0.9943 | 228 | 1.008 | 208.8 | 1.4957 | 232 | 1.5101 | 212.4 | 2.0787 | 236 | 2.0934 | 217.8 | 3.1007 | 242 | 3.1163 | 226.8 | 5.1112 | 252 | 5.1247
[8 empty] | 200.7 | 0.41152 | 223 | 0.42675 | 202.5 | 0.57824 | 225 | 0.59342 | 204.3 | 0.77011 | 227 | 0.78509 | 206.1 | 0.98571 | 229 | 0.99967 | 209.7 | 1.483 | 233 | 1.4997 | 213.3 | 2.061 | 237 | 2.0747 | 218.7 | 3.075 | 243 | 3.0913 | 227.7 | 5.0704 | 253 | 5.0851
[8 empty] | 201.6 | 0.40794 | 224 | 0.42467 | 203.4 | 0.57323 | 226 | 0.58717 | 205.2 | 0.76345 | 228 | 0.77675 | 207 | 0.97723 | 230 | 0.99134 | 210.6 | 1.4704 | 234 | 1.4851 | 214.2 | 2.0436 | 238 | 2.058 | 219.6 | 3.0495 | 244 | 3.0663 | 228.6 | 5.0301 | 254 | 5.0434
[8 empty] | 202.5 | 0.40441 | 225 | 0.41842 | 204.3 | 0.56827 | 227 | 0.583 | 206.1 | 0.75687 | 229 | 0.7705 | 207.9 | 0.96887 | 231 | 0.983 | 211.5 | 1.458 | 235 | 1.4747 | 215.1 | 2.0264 | 239 | 2.0413 | 220.5 | 3.0244 | 245 | 3.0413 | 229.5 | 4.9903 | 255 | 5.0038
[8 empty] | 203.4 | 0.40092 | 226 | 0.41634 | 205.2 | 0.56339 | 228 | 0.57675 | 207 | 0.75038 | 230 | 0.76634 | 208.8 | 0.96062 | 232 | 0.97467 | 212.4 | 1.4457 | 236 | 1.4601 | 216 | 2.0094 | 240 | 2.0247 | 221.4 | 2.9997 | 246 | 3.0163 | 230.4 | 4.9509 | 256 | 4.9663
[8 empty] | 204.3 | 0.39749 | 227 | 0.41217 | 206.1 | 0.55855 | 229 | 0.57467 | 207.9 | 0.74398 | 231 | 0.758 | 209.7 | 0.95246 | 233 | 0.96634 | 213.3 | 1.4336 | 237 | 1.4497 | 216.9 | 1.9928 | 241 | 2.008 | 222.3 | 2.9752 | 247 | 2.9913 | 231.3 | 4.912 | 257 | 4.9268
[8 empty] | 205.2 | 0.39409 | 228 | 0.408 | 207 | 0.55378 | 230 | 0.56842 | 208.8 | 0.73766 | 232 | 0.75175 | 210.6 | 0.94442 | 234 | 0.958 | 214.2 | 1.4217 | 238 | 1.4351 | 217.8 | 1.9765 | 242 | 1.9913 | 223.2 | 2.951 | 248 | 2.9663 | 232.2 | 4.8736 | 258 | 4.8872
[8 empty] | 206.1 | 0.39073 | 229 | 0.408 | 207.9 | 0.54908 | 231 | 0.56634 | 209.7 | 0.73141 | 233 | 0.7455 | 211.5 | 0.93647 | 235 | 0.95175 | 215.1 | 1.4099 | 239 | 1.4247 | 218.7 | 1.9603 | 243 | 1.9747 | 224.1 | 2.9271 | 249 | 2.9413 | 233.1 | 4.8356 | 259 | 4.8497
[8 empty] | 207 | 0.38742 | 230 | 0.40175 | 208.8 | 0.54444 | 232 | 0.558 | 210.6 | 0.72525 | 234 | 0.74134 | 212.4 | 0.92864 | 236 | 0.94342 | 216 | 1.3983 | 240 | 1.4122 | 219.6 | 1.9443 | 244 | 1.958 | 225 | 2.9035 | 250 | 2.9184 | 234 | 4.7981 | 260 | 4.8122
[8 empty] | 207.9 | 0.38416 | 231 | 0.39967 | 209.7 | 0.53984 | 233 | 0.55384 | 211.5 | 0.71917 | 235 | 0.733 | 213.3 | 0.92089 | 237 | 0.93509 | 216.9 | 1.3868 | 241 | 1.4018 | 220.5 | 1.9286 | 245 | 1.9434 | 225.9 | 2.8802 | 251 | 2.8934 | 234.9 | 4.761 | 261 | 4.7747
[8 empty] | 208.8 | 0.38093 | 232 | 0.3955 | 210.6 | 0.53532 | 234 | 0.54967 | 212.4 | 0.71318 | 236 | 0.72675 | 214.2 | 0.91325 | 238 | 0.92675 | 217.8 | 1.3754 | 242 | 1.3913 | 221.4 | 1.913 | 246 | 1.9268 | 226.8 | 2.8571 | 252 | 2.8705 | 235.8 | 4.7243 | 262 | 4.7413
[8 empty] | 209.7 | 0.37774 | 233 | 0.39134 | 211.5 | 0.53084 | 235 | 0.5455 | 213.3 | 0.70725 | 237 | 0.72467 | 215.1 | 0.9057 | 239 | 0.91842 | 218.7 | 1.3642 | 243 | 1.3788 | 222.3 | 1.8976 | 247 | 1.9122 | 227.7 | 2.8344 | 253 | 2.8497 | 236.7 | 4.688 | 263 | 4.7018
[8 empty] | 210.6 | 0.3746 | 234 | 0.39134 | 212.4 | 0.52644 | 236 | 0.54134 | 214.2 | 0.7014 | 238 | 0.71634 | 216 | 0.89825 | 240 | 0.91217 | 219.6 | 1.3531 | 244 | 1.3663 | 223.2 | 1.8824 | 248 | 1.8997 | 228.6 | 2.8119 | 254 | 2.8268 | 237.6 | 4.6522 | 264 | 4.6663
[8 empty] | 211.5 | 0.37149 | 235 | 0.38509 | 213.3 | 0.52209 | 237 | 0.53509 | 215.1 | 0.69561 | 239 | 0.71009 | 216.9 | 0.89089 | 241 | 0.908 | 220.5 | 1.3421 | 245 | 1.358 | 224.1 | 1.8674 | 249 | 1.883 | 229.5 | 2.7896 | 255 | 2.8038 | 238.5 | 4.6167 | 265 | 4.633
[8 empty] | 212.4 | 0.36844 | 236 | 0.383 | 214.2 | 0.51779 | 238 | 0.533 | 216 | 0.68991 | 240 | 0.70384 | 217.8 | 0.88362 | 242 | 0.89967 | 221.4 | 1.3313 | 246 | 1.3455 | 225 | 1.8526 | 250 | 1.8663 | 230.4 | 2.7677 | 256 | 2.783 | 239.4 | 4.5817 | 266 | 4.5955
[8 empty] | 213.3 | 0.36542 | 237 | 0.37884 | 215.1 | 0.51354 | 239 | 0.52675 | 216.9 | 0.68427 | 241 | 0.69967 | 218.7 | 0.87643 | 243 | 0.89134 | 222.3 | 1.3207 | 247 | 1.3351 | 225.9 | 1.8379 | 251 | 1.8518 | 231.3 | 2.746 | 257 | 2.7601 | 240.3 | 4.547 | 267 | 4.5601
[8 empty] | 214.2 | 0.36243 | 238 | 0.37675 | 216 | 0.50935 | 240 | 0.52467 | 217.8 | 0.6787 | 242 | 0.69342 | 219.6 | 0.86934 | 244 | 0.883 | 223.2 | 1.3101 | 248 | 1.3247 | 226.8 | 1.8234 | 252 | 1.8372 | 232.2 | 2.7245 | 258 | 2.7413 | 241.2 | 4.5128 | 268 | 4.5268
[8 empty] | 215.1 | 0.35948 | 239 | 0.37467 | 216.9 | 0.5052 | 241 | 0.51842 | 218.7 | 0.67321 | 243 | 0.68717 | 220.5 | 0.86233 | 245 | 0.87675 | 224.1 | 1.2997 | 249 | 1.3163 | 227.7 | 1.8091 | 253 | 1.8247 | 233.1 | 2.7033 | 259 | 2.7184 | 242.1 | 4.4789 | 269 | 4.4934
[8 empty] | 216 | 0.35657 | 240 | 0.3705 | 217.8 | 0.50112 | 242 | 0.51634 | 219.6 | 0.66778 | 244 | 0.683 | 221.4 | 0.85542 | 246 | 0.86842 | 225 | 1.2894 | 250 | 1.3038 | 228.6 | 1.795 | 254 | 1.8101 | 234 | 2.6823 | 260 | 2.6997 | 243 | 4.4454 | 270 | 4.4601
[8 empty] | 216.9 | 0.35369 | 241 | 0.36842 | 218.7 | 0.49707 | 243 | 0.51009 | 220.5 | 0.6624 | 245 | 0.67675 | 222.3 | 0.84858 | 247 | 0.86217 | 225.9 | 1.2792 | 251 | 1.2934 | 229.5 | 1.781 | 255 | 1.7955 | 234.9 | 2.6616 | 261 | 2.6768 | 243.9 | 4.4123 | 271 | 4.4268
[8 empty] | 217.8 | 0.35085 | 242 | 0.36634 | 219.6 | 0.49308 | 244 | 0.508 | 221.4 | 0.65711 | 246 | 0.6705 | 223.2 | 0.84184 | 248 | 0.858 | 226.8 | 1.2691 | 252 | 1.283 | 230.4 | 1.7672 | 256 | 1.783 | 235.8 | 2.6411 | 262 | 2.658 | 244.8 | 4.3796 | 272 | 4.3934
[8 empty] | 218.7 | 0.34804 | 243 | 0.36217 | 220.5 | 0.48914 | 245 | 0.50384 | 222.3 | 0.65189 | 247 | 0.66634 | 224.1 | 0.83515 | 249 | 0.84967 | 227.7 | 1.2592 | 253 | 1.2747 | 231.3 | 1.7535 | 257 | 1.7684 | 236.7 | 2.6209 | 263 | 2.6351 | 245.7 | 4.3472 | 273 | 4.3601
[8 empty] | 219.6 | 0.34527 | 244 | 0.36009 | 221.4 | 0.48526 | 246 | 0.49967 | 223.2 | 0.64672 | 248 | 0.66009 | 225 | 0.82856 | 250 | 0.84342 | 228.6 | 1.2494 | 254 | 1.2663 | 232.2 | 1.7401 | 258 | 1.7538 | 237.6 | 2.6009 | 264 | 2.6163 | 246.6 | 4.3152 | 274 | 4.3288
[8 empty] | 220.5 | 0.32875 | 245 | 0.358 | 222.3 | 0.48141 | 247 | 0.4955 | 224.1 | 0.64161 | 249 | 0.658 | 225.9 | 0.82205 | 251 | 0.83509 | 229.5 | 1.2397 | 255 | 1.2538 | 233.1 | 1.7267 | 259 | 1.7413 | 238.5 | 2.5811 | 265 | 2.5955 | 247.5 | 4.2835 | 275 | 4.2997
[8 empty] | 221.4 | 0.31229 | 246 | 0.35175 | 223.2 | 0.47762 | 248 | 0.49134 | 225 | 0.63656 | 250 | 0.65175 | 226.8 | 0.81561 | 252 | 0.833 | 230.4 | 1.2301 | 256 | 1.2434 | 234 | 1.7135 | 260 | 1.7268 | 239.4 | 2.5616 | 266 | 2.5768 | 248.4 | 4.2522 | 276 | 4.2663
[8 empty] | 222.3 | 0.30069 | 247 | 0.35175 | 224.1 | 0.47386 | 249 | 0.48717 | 225.9 | 0.63156 | 251 | 0.6455 | 227.7 | 0.80925 | 253 | 0.82467 | 231.3 | 1.2206 | 257 | 1.2351 | 234.9 | 1.7005 | 261 | 1.7163 | 240.3 | 2.5422 | 267 | 2.558 | 249.3 | 4.2212 | 277 | 4.2351
[8 empty] | 223.2 | 0.29384 | 248 | 0.34967 | 225 | 0.47015 | 250 | 0.48509 | 226.8 | 0.62663 | 252 | 0.64134 | 228.6 | 0.80296 | 254 | 0.81634 | 232.2 | 1.2112 | 258 | 1.2247 | 235.8 | 1.6876 | 262 | 1.7018 | 241.2 | 2.5231 | 268 | 2.5372 | 250.2 | 4.1905 | 278 | 4.208
[8 empty] | 224.1 | 0.28708 | 249 | 0.34134 | 225.9 | 0.46649 | 251 | 0.483 | 227.7 | 0.62176 | 253 | 0.63509 | 229.5 | 0.79675 | 255 | 0.81009 | 233.1 | 1.202 | 259 | 1.2163 | 236.7 | 1.6749 | 263 | 1.6913 | 242.1 | 2.5042 | 269 | 2.5184 | 250.2 | 0.0072687 | 279 | 4.1747
[8 empty] | 225 | 0.047409 | 250 | 0.06231 | 226.8 | 0.46286 | 252 | 0.47675 | 228.6 | 0.61695 | 254 | 0.633 | 230.4 | 0.79061 | 256 | 0.808 | 234 | 1.1928 | 260 | 1.208 | 237.6 | 1.6623 | 264 | 1.6768 | 243 | 2.4855 | 270 | 2.4997 | 468 | 0.003 | 280 | 4.1434
[8 empty] | 225.9 | 0.047167 | 500 | 0.052 | 227.7 | 0.45929 | 253 | 0.47467 | 229.5 | 0.6122 | 255 | 0.62675 | 231.3 | 0.78454 | 257 | 0.79967 | 234.9 | 1.1837 | 261 | 1.1997 | 238.5 | 1.6498 | 265 | 1.6663 | 243.9 | 2.467 | 271 | 2.483 | 6300 | 0.003 | 281 | 4.1163
[8 empty] | 226.8 | 0.047163 | 500 | 0.033 | 228.6 | 0.45575 | 254 | 0.4705 | 230.4 | 0.60749 | 256 | 0.62467 | 232.2 | 0.77854 | 258 | 0.79342 | 235.8 | 1.1748 | 262 | 1.1913 | 239.4 | 1.6375 | 266 | 1.6518 | 244.8 | 2.4487 | 272 | 2.4622 |  |  | 282 | 4.0851
[8 empty] | 227.7 | 0.047088 | 1000 | 0.033 | 229.5 | 0.45226 | 255 | 0.46634 | 231.3 | 0.60286 | 257 | 0.61634 | 233.1 | 0.77261 | 259 | 0.78717 | 236.7 | 1.166 | 263 | 1.183 | 240.3 | 1.6253 | 267 | 1.6413 | 245.7 | 2.4307 | 273 | 2.4434 |  |  | 283 | 4.058
[8 empty] | 228.6 | 0.046617 | 6300 | 0.022 | 230.4 | 0.4488 | 256 | 0.46217 | 232.2 | 0.59826 | 258 | 0.61217 | 234 | 0.76676 | 260 | 0.783 | 237.6 | 1.1572 | 264 | 1.1705 | 241.2 | 1.6133 | 268 | 1.6268 | 246.6 | 2.4128 | 274 | 2.4268 |  |  | 284 | 4.0268
[8 empty] | 229.5 | 0.046613 |  |  | 231.3 | 0.44539 | 257 | 0.46009 | 233.1 | 0.59372 | 259 | 0.608 | 234.9 | 0.76096 | 261 | 0.77467 | 238.5 | 1.1486 | 265 | 1.1622 | 242.1 | 1.6014 | 269 | 1.6163 | 247.5 | 2.3951 | 275 | 2.4101 |  |  | 285 | 3.9997
[8 empty] | 230.4 | 0.046608 |  |  | 232.2 | 0.44202 | 258 | 0.458 | 234 | 0.58923 | 260 | 0.60384 | 235.8 | 0.75523 | 262 | 0.76842 | 239.4 | 1.14 | 266 | 1.1538 | 243 | 1.5896 | 270 | 1.6038 | 248.4 | 2.3776 | 276 | 2.3913 |  |  | 286 | 3.9705
[8 empty] | 231.3 | 0.046138 |  |  | 233.1 | 0.43867 | 259 | 0.45175 | 234.9 | 0.5848 | 261 | 0.59967 | 236.7 | 0.74958 | 263 | 0.76634 | 240.3 | 1.1316 | 267 | 1.1455 | 243.9 | 1.578 | 271 | 1.5913 | 249.3 | 2.3603 | 277 | 2.3747 |  |  | 287 | 3.9434
[8 empty] | 232.2 | 0.046133 |  |  | 234 | 0.43539 | 260 | 0.44967 | 235.8 | 0.58041 | 262 | 0.59342 | 237.6 | 0.74397 | 264 | 0.758 | 241.2 | 1.1232 | 268 | 1.1372 | 244.8 | 1.5665 | 272 | 1.583 | 250.2 | 2.3432 | 278 | 2.358 |  |  | 288 | 3.9163
[8 empty] | 233.1 | 0.046129 |  |  | 234.9 | 0.43213 | 261 | 0.4455 | 236.7 | 0.57609 | 263 | 0.59134 | 238.5 | 0.73844 | 265 | 0.75175 | 242.1 | 1.1149 | 269 | 1.1288 | 245.7 | 1.5551 | 273 | 1.5684 | 250.2 | 0.0072687 | 279 | 2.3413 |  |  | 289 | 3.8913
[8 empty] | 234 | 0.046126 |  |  | 235.8 | 0.4289 | 262 | 0.44342 | 237.6 | 0.57179 | 264 | 0.58509 | 239.4 | 0.73297 | 266 | 0.74967 | 243 | 1.1067 | 270 | 1.1205 | 246.6 | 1.5438 | 274 | 1.558 | 468 | 0.003 | 280 | 2.3247 |  |  | 290 | 3.8601
[8 empty] | 234.9 | 0.046122 |  |  | 236.7 | 0.42572 | 263 | 0.44134 | 238.5 | 0.56756 | 265 | 0.583 | 240.3 | 0.72755 | 267 | 0.74134 | 243.9 | 1.0987 | 271 | 1.1122 | 247.5 | 1.5327 | 275 | 1.5497 | 6300 | 0.003 | 281 | 2.308 |  |  | 291 | 3.8351
[8 empty] | 235.8 | 0.04612 |  |  | 237.6 | 0.42257 | 264 | 0.43717 | 239.4 | 0.56337 | 266 | 0.57675 | 241.2 | 0.7222 | 268 | 0.73509 | 244.8 | 1.0907 | 272 | 1.108 | 248.4 | 1.5217 | 276 | 1.5351 |  |  | 282 | 2.2913 |  |  | 292 | 3.808
[8 empty] | 236.7 | 0.045648 |  |  | 238.5 | 0.41945 | 265 | 0.433 | 240.3 | 0.55922 | 267 | 0.57467 | 242.1 | 0.71691 | 269 | 0.733 | 245.7 | 1.0828 | 273 | 1.0997 | 249.3 | 1.5108 | 277 | 1.5247 |  |  | 283 | 2.2747 |  |  | 293 | 3.783
[8 empty] | 237.6 | 0.045645 |  |  | 239.4 | 0.41638 | 266 | 0.433 | 241.2 | 0.55512 | 268 | 0.56842 | 243 | 0.71168 | 270 | 0.72675 | 246.6 | 1.075 | 274 | 1.0913 | 250.2 | 1.5 | 278 | 1.5163 |  |  | 284 | 2.258 |  |  | 294 | 3.758
[8 empty] | 238.5 | 0.045642 |  |  | 240.3 | 0.41333 | 267 | 0.42675 | 242.1 | 0.55107 | 269 | 0.56634 | 243.9 | 0.70651 | 271 | 0.7205 | 247.5 | 1.0672 | 275 | 1.083 | 250.2 | 0.0072687 | 279 | 1.5038 |  |  | 285 | 2.2434 |  |  | 295 | 3.733
[8 empty] | 239.4 | 0.045639 |  |  | 241.2 | 0.41032 | 268 | 0.42467 | 243 | 0.54706 | 270 | 0.56009 | 244.8 | 0.70139 | 272 | 0.71634 | 248.4 | 1.0596 | 276 | 1.0747 | 468 | 0.003 | 280 | 1.4934 |  |  | 286 | 2.2268 |  |  | 296 | 3.708
[8 empty] | 240.3 | 0.045635 |  |  | 242.1 | 0.40734 | 269 | 0.42467 | 243.9 | 0.5431 | 271 | 0.558 | 245.7 | 0.69634 | 273 | 0.71009 | 249.3 | 1.052 | 277 | 1.0663 | 6300 | 0.003 | 281 | 1.483 |  |  | 287 | 2.2101 |  |  | 297 | 3.683
[8 empty] | 241.2 | 0.045632 |  |  | 243 | 0.4044 | 270 | 0.41842 | 244.8 | 0.53919 | 272 | 0.55384 | 246.6 | 0.69134 | 274 | 0.708 | 250.2 | 1.0445 | 278 | 1.058 |  |  | 282 | 1.4747 |  |  | 288 | 2.1955 |  |  | 298 | 3.658
[8 empty] | 242.1 | 0.045628 |  |  | 243.9 | 0.40149 | 271 | 0.41634 | 245.7 | 0.53533 | 273 | 0.54967 | 247.5 | 0.68638 | 275 | 0.69967 | 250.2 | 0.0072687 | 279 | 1.0518 |  |  | 283 | 1.4622 |  |  | 289 | 2.183 |  |  | 299 | 3.633
[8 empty] | 243 | 0.045625 |  |  | 244.8 | 0.39861 | 272 | 0.41217 | 246.6 | 0.53149 | 274 | 0.5455 | 248.4 | 0.68148 | 276 | 0.6955 | 468 | 0.003 | 280 | 1.0434 |  |  | 284 | 1.4518 |  |  | 290 | 2.1663 |  |  | 300 | 0.06231
[8 empty] | 243.9 | 0.045154 |  |  | 245.7 | 0.39578 | 273 | 0.41009 | 247.5 | 0.5277 | 275 | 0.54134 | 249.3 | 0.67663 | 277 | 0.69134 | 6300 | 0.003 | 281 | 1.0372 |  |  | 285 | 1.4413 |  |  | 291 | 2.1518 |  |  | 500 | 0.057
[8 empty] | 244.8 | 0.045152 |  |  | 246.6 | 0.39296 | 274 | 0.408 | 248.4 | 0.52395 | 276 | 0.54134 | 250.2 | 0.67183 | 278 | 0.68509 |  |  | 282 | 1.0288 |  |  | 286 | 1.433 |  |  | 292 | 2.1351 |  |  | 500 | 0.033
[8 empty] | 245.7 | 0.045148 |  |  | 247.5 | 0.39018 | 275 | 0.40384 | 249.3 | 0.52024 | 277 | 0.53509 | 250.2 | 0.0072687 | 279 | 0.683 |  |  | 283 | 1.0247 |  |  | 287 | 1.4247 |  |  | 293 | 2.1247 |  |  | 1000 | 0.033
[8 empty] | 246.6 | 0.045145 |  |  | 248.4 | 0.38741 | 276 | 0.40175 | 250.2 | 0.51656 | 278 | 0.533 | 468 | 0.003 | 280 | 0.67675 |  |  | 284 | 1.0163 |  |  | 288 | 1.4122 |  |  | 294 | 2.108 |  |  | 6300 | 0.022
[8 empty] | 247.5 | 0.045142 |  |  | 249.3 | 0.3847 | 277 | 0.39967 | 250.2 | 0.0072687 | 279 | 0.52675 | 6300 | 0.003 | 281 | 0.67467 |  |  | 285 | 1.008 |  |  | 289 | 1.4018 |  |  | 295 | 2.0934
[8 empty] | 248.4 | 0.045139 |  |  | 250.2 | 0.38199 | 278 | 0.3955 | 468 | 0.003 | 280 | 0.52467 |  |  | 282 | 0.66842 |  |  | 286 | 1.0018 |  |  | 290 | 1.3934 |  |  | 296 | 2.0768
[8 empty] | 249.3 | 0.045136 |  |  | 250.2 | 0.0072687 | 279 | 0.39342 | 6300 | 0.003 | 281 | 0.5205 |  |  | 283 | 0.66217 |  |  | 287 | 0.99342 |  |  | 291 | 1.383 |  |  | 297 | 2.0663
[8 empty] | 250.2 | 0.039364 |  |  | 468 | 0.003 | 280 | 0.39134 |  |  | 282 | 0.51634 |  |  | 284 | 0.658 |  |  | 288 | 0.98717 |  |  | 292 | 1.3747 |  |  | 298 | 2.0497
[8 empty] | 250.2 | 0.0072687 |  |  | 6300 | 0.003 | 281 | 0.39134 |  |  | 283 | 0.51217 |  |  | 285 | 0.65384 |  |  | 289 | 0.983 |  |  | 293 | 1.3663 |  |  | 299 | 2.033
[8 empty] | 468 | 0.003 |  |  |  |  | 282 | 0.38509 |  |  | 284 | 0.51009 |  |  | 286 | 0.64967 |  |  | 290 | 0.97467 |  |  | 294 | 1.358 |  |  | 300 | 0.06231
[8 empty] | 6300 | 0.003 |  |  |  |  | 283 | 0.383 |  |  | 285 | 0.508 |  |  | 287 | 0.6455 |  |  | 291 | 0.96842 |  |  | 295 | 1.3497 |  |  | 500 | 0.057
[14 empty] | 284 | 0.383 |  |  | 286 | 0.50175 |  |  | 288 | 0.64134 |  |  | 292 | 0.96217 |  |  | 296 | 1.3413 |  |  | 500 | 0.033
[14 empty] | 285 | 0.37675 |  |  | 287 | 0.49967 |  |  | 289 | 0.63509 |  |  | 293 | 0.958 |  |  | 297 | 1.3268 |  |  | 1000 | 0.033
[14 empty] | 286 | 0.37675 |  |  | 288 | 0.4955 |  |  | 290 | 0.633 |  |  | 294 | 0.94967 |  |  | 298 | 1.3163 |  |  | 6300 | 0.022
[14 empty] | 287 | 0.37467 |  |  | 289 | 0.49342 |  |  | 291 | 0.62675 |  |  | 295 | 0.94342 |  |  | 299 | 1.308
[14 empty] | 288 | 0.3705 |  |  | 290 | 0.49134 |  |  | 292 | 0.62467 |  |  | 296 | 0.93509 |  |  | 300 | 0.06231
[14 empty] | 289 | 0.36842 |  |  | 291 | 0.48509 |  |  | 293 | 0.6205 |  |  | 297 | 0.933 |  |  | 500 | 0.057
[14 empty] | 290 | 0.36634 |  |  | 292 | 0.483 |  |  | 294 | 0.61634 |  |  | 298 | 0.92467 |  |  | 500 | 0.033
[14 empty] | 291 | 0.36634 |  |  | 293 | 0.483 |  |  | 295 | 0.61009 |  |  | 299 | 0.91634 |  |  | 1000 | 0.033
[14 empty] | 292 | 0.36009 |  |  | 294 | 0.47675 |  |  | 296 | 0.608 |  |  | 300 | 0.06231 |  |  | 6300 | 0.022
[14 empty] | 293 | 0.36009 |  |  | 295 | 0.47467 |  |  | 297 | 0.60175 |  |  | 500 | 0.057
[14 empty] | 294 | 0.358 |  |  | 296 | 0.46842 |  |  | 298 | 0.59967 |  |  | 500 | 0.033
[14 empty] | 295 | 0.35175 |  |  | 297 | 0.46842 |  |  | 299 | 0.59134 |  |  | 1000 | 0.033
[14 empty] | 296 | 0.35175 |  |  | 298 | 0.46634 |  |  | 300 | 0.06231 |  |  | 6300 | 0.022
[14 empty] | 297 | 0.34967 |  |  | 299 | 0.458 |  |  | 500 | 0.057
[14 empty] | 298 | 0.34967 |  |  | 300 | 0.06231 |  |  | 500 | 0.033
[14 empty] | 299 | 0.34134 |  |  | 500 | 0.057 |  |  | 1000 | 0.033
[14 empty] | 300 | 0.06231 |  |  | 500 | 0.033 |  |  | 6300 | 0.022
[14 empty] | 500 | 0.057 |  |  | 1000 | 0.033
[14 empty] | 500 | 0.033 |  |  | 6300 | 0.022
[14 empty] | 1000 | 0.033
[14 empty] | 6300 | 0.022

## S&C "K" Speed
S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter
S&C "K" Speed | [11 empty] | S&C "K" Speed | [11 empty] | S&C "K" Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025
Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information.
2K |  |  |  | 3K |  |  |  | 5K |  |  |  | 6K |  |  |  | 8K |  |  |  | 10K |  |  |  | 12K |  |  |  | 15K |  |  |  | 20K
Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s
4 | 9.653 | 5 | 9.669 | 6 | 20.934 | 7 | 20.951 | 9.9 | 25.767 | 11 | 25.783 | 11.7 | 216.742 | 13 | 216.759 | 14.4 | 344.067 | 16 | 344.083 | 18.9 | 444.3953 | 21 | 444.4108 | 26.1 | 89.7831 | 29 | 89.7997 | 30.6 | 783.8235 | 34 | 783.8399 | 39.6 | 999.5608 | 44 | 999.5774
5 | 4.127 | 6 | 4.141 | 7 | 8.025 | 8 | 8.041 | 10.8 | 8.217 | 12 | 8.233 | 12.6 | 18.983 | 14 | 18.996 | 15.3 | 30.344 | 17 | 30.36 | 19.8 | 39.4743 | 22 | 39.4872 | 27 | 33.0999 | 30 | 33.1163 | 31.5 | 70.2544 | 35 | 70.2684 | 40.5 | 89.8768 | 45 | 89.8934
6 | 2.465 | 7 | 2.479 | 8 | 4.728 | 9 | 4.741 | 11.7 | 4.726 | 13 | 4.741 | 13.5 | 9.594 | 15 | 9.61 | 16.2 | 15.432 | 18 | 15.446 | 20.7 | 20.2131 | 23 | 20.2268 | 27.9 | 20.032 | 31 | 20.0455 | 32.4 | 36.2798 | 36 | 36.2934 | 41.4 | 46.5598 | 46 | 46.5768
7 | 1.685 | 8 | 1.7 | 9 | 3.242 | 10 | 3.258 | 12.6 | 3.242 | 14 | 3.258 | 14.4 | 6.279 | 16 | 6.293 | 17.1 | 10.159 | 19 | 10.175 | 21.6 | 13.3922 | 24 | 13.408 | 28.8 | 14.2319 | 32 | 14.2455 | 33.3 | 24.2347 | 37 | 24.2497 | 42.3 | 31.1978 | 47 | 31.2122
8 | 1.242 | 9 | 1.258 | 9.9 | 2.408 | 11 | 2.425 | 13.5 | 2.425 | 15 | 2.441 | 15.3 | 4.592 | 17 | 4.608 | 18 | 7.47 | 20 | 7.485 | 22.5 | 9.9086 | 25 | 9.9247 | 29.7 | 10.9595 | 33 | 10.9747 | 34.2 | 18.0724 | 38 | 18.0851 | 43.2 | 23.3352 | 48 | 23.3518
9 | 0.961 | 10 | 0.975 | 10.8 | 1.879 | 12 | 1.893 | 14.4 | 1.912 | 16 | 1.927 | 16.2 | 3.575 | 18 | 3.591 | 18.9 | 5.846 | 21 | 5.86 | 23.4 | 7.7986 | 26 | 7.8122 | 30.6 | 8.8607 | 34 | 8.8768 | 35.1 | 14.3321 | 39 | 14.3455 | 44.1 | 18.5606 | 49 | 18.5768
9.9 | 0.769 | 11 | 0.783 | 11.7 | 1.518 | 13 | 1.533 | 15.3 | 1.561 | 17 | 1.575 | 17.1 | 2.897 | 19 | 2.91 | 19.8 | 4.761 | 22 | 4.775 | 24.3 | 6.3863 | 27 | 6.4018 | 31.5 | 7.4017 | 35 | 7.4163 | 36 | 11.8227 | 40 | 11.8372 | 45 | 15.3548 | 50 | 15.3684
10.8 | 0.632 | 12 | 0.646 | 12.6 | 1.258 | 14 | 1.275 | 16.2 | 1.307 | 18 | 1.325 | 18 | 2.416 | 20 | 2.433 | 20.7 | 3.987 | 23 | 4.002 | 25.2 | 5.3765 | 28 | 5.3913 | 32.4 | 6.3298 | 36 | 6.3434 | 36.9 | 10.0239 | 41 | 10.0413 | 45.9 | 13.0551 | 51 | 13.0684
11.7 | 0.53 | 13 | 0.543 | 13.5 | 1.062 | 15 | 1.077 | 17.1 | 1.116 | 19 | 1.133 | 18.9 | 2.056 | 21 | 2.071 | 21.6 | 3.409 | 24 | 3.425 | 26.1 | 4.6199 | 29 | 4.6351 | 33.3 | 5.5099 | 37 | 5.5247 | 37.8 | 8.6723 | 42 | 8.6851 | 46.8 | 11.3257 | 52 | 11.3413
12.6 | 0.451 | 14 | 0.466 | 14.4 | 0.912 | 16 | 0.927 | 18 | 0.967 | 20 | 0.983 | 19.8 | 1.78 | 22 | 1.793 | 22.5 | 2.961 | 25 | 2.977 | 27 | 4.0329 | 30 | 4.0497 | 34.2 | 4.863 | 38 | 4.8768 | 38.7 | 7.6205 | 43 | 7.6351 | 47.7 | 9.9786 | 53 | 9.9934
13.5 | 0.39 | 15 | 0.404 | 15.3 | 0.792 | 17 | 0.808 | 18.9 | 0.849 | 21 | 0.862 | 20.7 | 1.56 | 23 | 1.575 | 23.4 | 2.606 | 26 | 2.621 | 27.9 | 3.5649 | 31 | 3.5788 | 35.1 | 4.3401 | 39 | 4.3538 | 39.6 | 6.7792 | 44 | 6.7934 | 48.6 | 8.9 | 54 | 8.9163
14.4 | 0.34 | 16 | 0.354 | 16.2 | 0.696 | 18 | 0.71 | 19.8 | 0.752 | 22 | 0.766 | 21.6 | 1.382 | 24 | 1.396 | 24.3 | 2.317 | 27 | 2.333 | 28.8 | 3.1836 | 32 | 3.1997 | 36 | 3.9091 | 40 | 3.9247 | 40.5 | 6.0915 | 45 | 6.108 | 49.5 | 8.0176 | 55 | 8.033
15.3 | 0.3 | 17 | 0.316 | 17.1 | 0.617 | 19 | 0.633 | 20.7 | 0.673 | 23 | 0.687 | 22.5 | 1.236 | 25 | 1.25 | 25.2 | 2.078 | 28 | 2.093 | 29.7 | 2.8674 | 33 | 2.883 | 36.9 | 3.5481 | 41 | 3.5622 | 41.4 | 5.5193 | 46 | 5.533 | 50.4 | 7.2826 | 56 | 7.2997
16.2 | 0.267 | 18 | 0.283 | 18 | 0.551 | 20 | 0.566 | 21.6 | 0.606 | 24 | 0.618 | 23.4 | 1.113 | 26 | 1.127 | 26.1 | 1.878 | 29 | 1.891 | 30.6 | 2.6012 | 34 | 2.6163 | 37.8 | 3.2414 | 42 | 3.258 | 42.3 | 5.0359 | 47 | 5.0497 | 51.3 | 6.661 | 57 | 6.6768
17.1 | 0.24 | 19 | 0.254 | 18.9 | 0.496 | 21 | 0.51 | 22.5 | 0.549 | 25 | 0.562 | 24.3 | 1.009 | 27 | 1.025 | 27 | 1.708 | 30 | 1.725 | 31.5 | 2.3745 | 35 | 2.3913 | 38.7 | 2.978 | 43 | 2.9934 | 43.2 | 4.6226 | 48 | 4.6372 | 52.2 | 6.1289 | 58 | 6.1434
18 | 0.216 | 20 | 0.233 | 19.8 | 0.449 | 22 | 0.462 | 23.4 | 0.5 | 26 | 0.516 | 25.2 | 0.92 | 28 | 0.935 | 27.9 | 1.562 | 31 | 1.577 | 32.4 | 2.1793 | 36 | 2.1934 | 39.6 | 2.7495 | 44 | 2.7663 | 44.1 | 4.2652 | 49 | 4.283 | 53.1 | 5.6683 | 59 | 5.683
18.9 | 0.196 | 21 | 0.21 | 20.7 | 0.408 | 23 | 0.425 | 24.3 | 0.458 | 27 | 0.475 | 26.1 | 0.843 | 29 | 0.858 | 28.8 | 1.435 | 32 | 1.45 | 33.3 | 2.0095 | 37 | 2.0247 | 40.5 | 2.5495 | 45 | 2.5663 | 45 | 3.9534 | 50 | 3.9684 | 54 | 5.2659 | 60 | 5.283
19.8 | 0.179 | 22 | 0.193 | 21.6 | 0.374 | 24 | 0.387 | 25.2 | 0.422 | 28 | 0.435 | 27 | 0.776 | 30 | 0.791 | 29.7 | 1.324 | 33 | 1.337 | 34.2 | 1.8607 | 38 | 1.8747 | 41.4 | 2.3731 | 46 | 2.3872 | 45.9 | 3.6792 | 51 | 3.6934 | 54.9 | 4.9115 | 61 | 4.9268
20.7 | 0.164 | 23 | 0.181 | 22.5 | 0.343 | 25 | 0.358 | 26.1 | 0.39 | 29 | 0.404 | 27.9 | 0.717 | 31 | 0.733 | 30.6 | 1.227 | 34 | 1.241 | 35.1 | 1.7293 | 39 | 1.7434 | 42.3 | 2.2165 | 47 | 2.233 | 46.8 | 3.4362 | 52 | 3.4497 | 55.8 | 4.597 | 62 | 4.6101
21.6 | 0.151 | 24 | 0.166 | 23.4 | 0.316 | 26 | 0.333 | 27 | 0.361 | 30 | 0.375 | 28.8 | 0.665 | 32 | 0.679 | 31.5 | 1.14 | 35 | 1.154 | 36 | 1.6126 | 40 | 1.6268 | 43.2 | 2.0766 | 48 | 2.0913 | 47.7 | 3.2195 | 53 | 3.233 | 56.7 | 4.3163 | 63 | 4.333
22.5 | 0.139 | 25 | 0.157 | 24.3 | 0.293 | 27 | 0.308 | 27.9 | 0.336 | 31 | 0.35 | 29.7 | 0.619 | 33 | 0.633 | 32.4 | 1.063 | 36 | 1.077 | 36.9 | 1.5083 | 41 | 1.5247 | 44.1 | 1.9509 | 49 | 1.9663 | 48.6 | 3.0252 | 54 | 3.0413 | 57.6 | 4.0642 | 64 | 4.0788
23.4 | 0.129 | 26 | 0.144 | 25.2 | 0.272 | 28 | 0.285 | 28.8 | 0.313 | 32 | 0.327 | 30.6 | 0.578 | 34 | 0.591 | 33.3 | 0.995 | 37 | 1.008 | 37.8 | 1.4146 | 42 | 1.4288 | 45 | 1.8374 | 50 | 1.8518 | 49.5 | 2.8501 | 55 | 2.8663 | 58.5 | 3.8366 | 65 | 3.8518
24.3 | 0.12 | 27 | 0.135 | 26.1 | 0.253 | 29 | 0.266 | 29.7 | 0.293 | 33 | 0.308 | 31.5 | 0.541 | 35 | 0.558 | 34.2 | 0.933 | 38 | 0.95 | 38.7 | 1.3301 | 43 | 1.3434 | 45.9 | 1.7346 | 51 | 1.7497 | 50.4 | 2.6914 | 56 | 2.708 | 59.4 | 3.6303 | 66 | 3.6434
25.2 | 0.112 | 28 | 0.127 | 27 | 0.236 | 30 | 0.25 | 30.6 | 0.275 | 34 | 0.291 | 32.4 | 0.508 | 36 | 0.525 | 35.1 | 0.877 | 39 | 0.891 | 39.6 | 1.2535 | 44 | 1.2684 | 46.8 | 1.641 | 52 | 1.658 | 51.3 | 2.5472 | 57 | 2.5601 | 60.3 | 3.4424 | 67 | 3.458
26.1 | 0.105 | 29 | 0.119 | 27.9 | 0.221 | 31 | 0.235 | 31.5 | 0.259 | 35 | 0.275 | 33.3 | 0.477 | 37 | 0.491 | 36 | 0.826 | 40 | 0.841 | 40.5 | 1.1839 | 45 | 1.1997 | 47.7 | 1.5556 | 53 | 1.5684 | 52.2 | 2.4155 | 58 | 2.433 | 61.2 | 3.2706 | 68 | 3.2851
27 | 0.099 | 30 | 0.116 | 28.8 | 0.208 | 32 | 0.225 | 32.4 | 0.244 | 36 | 0.258 | 34.2 | 0.45 | 38 | 0.466 | 36.9 | 0.779 | 41 | 0.793 | 41.4 | 1.1202 | 46 | 1.1351 | 48.6 | 1.4772 | 54 | 1.4913 | 53.1 | 2.2949 | 59 | 2.3101 | 62.1 | 3.113 | 69 | 3.1268
27.9 | 0.093 | 31 | 0.109 | 29.7 | 0.196 | 33 | 0.21 | 33.3 | 0.23 | 37 | 0.243 | 35.1 | 0.425 | 39 | 0.441 | 37.8 | 0.737 | 42 | 0.752 | 42.3 | 1.062 | 47 | 1.0768 | 49.5 | 1.4052 | 55 | 1.4184 | 54 | 2.184 | 60 | 2.1997 | 63 | 2.968 | 70 | 2.983
28.8 | 0.088 | 32 | 0.102 | 30.6 | 0.184 | 34 | 0.2 | 34.2 | 0.218 | 38 | 0.233 | 36 | 0.402 | 40 | 0.416 | 38.7 | 0.698 | 43 | 0.712 | 43.2 | 1.0084 | 48 | 1.0247 | 50.4 | 1.3387 | 56 | 1.3518 | 54.9 | 2.0817 | 61 | 2.0955 | 63.9 | 2.8341 | 71 | 2.8497
29.7 | 0.083 | 33 | 0.1 | 31.5 | 0.174 | 35 | 0.191 | 35.1 | 0.206 | 39 | 0.221 | 36.9 | 0.381 | 41 | 0.396 | 39.6 | 0.663 | 44 | 0.677 | 44.1 | 0.95912 | 49 | 0.97467 | 51.3 | 1.2773 | 57 | 1.2913 | 55.8 | 1.9872 | 62 | 2.0018 | 64.8 | 2.7101 | 72 | 2.7247
30.6 | 0.079 | 34 | 0.093 | 32.4 | 0.165 | 36 | 0.182 | 36 | 0.196 | 40 | 0.21 | 37.8 | 0.362 | 42 | 0.377 | 40.5 | 0.63 | 45 | 0.643 | 45 | 0.91351 | 50 | 0.92675 | 52.2 | 1.2203 | 58 | 1.2351 | 56.7 | 1.8996 | 63 | 1.9163 | 65.7 | 2.5951 | 73 | 2.6101
31.5 | 0.075 | 35 | 0.091 | 33.3 | 0.156 | 37 | 0.173 | 36.9 | 0.186 | 41 | 0.201 | 38.7 | 0.344 | 43 | 0.358 | 41.4 | 0.6 | 46 | 0.616 | 45.9 | 0.87134 | 51 | 0.88509 | 53.1 | 1.1674 | 59 | 1.183 | 57.6 | 1.8182 | 64 | 1.833 | 66.6 | 2.4881 | 74 | 2.5018
32.4 | 0.071 | 36 | 0.086 | 34.2 | 0.148 | 38 | 0.165 | 37.8 | 0.177 | 42 | 0.193 | 39.6 | 0.327 | 44 | 0.341 | 42.3 | 0.572 | 47 | 0.585 | 46.8 | 0.83216 | 52 | 0.8455 | 54 | 1.1181 | 60 | 1.133 | 58.5 | 1.7423 | 65 | 1.758 | 67.5 | 2.3883 | 75 | 2.4018
33.3 | 0.068 | 37 | 0.083 | 35.1 | 0.141 | 39 | 0.158 | 38.7 | 0.169 | 43 | 0.184 | 40.5 | 0.312 | 45 | 0.327 | 43.2 | 0.546 | 48 | 0.56 | 47.7 | 0.79579 | 53 | 0.81009 | 54.9 | 1.0721 | 61 | 1.0851 | 59.4 | 1.6716 | 66 | 1.6851 | 68.4 | 2.295 | 76 | 2.3101
34.2 | 0.065 | 38 | 0.082 | 36 | 0.134 | 40 | 0.15 | 39.6 | 0.161 | 44 | 0.177 | 41.4 | 0.298 | 46 | 0.312 | 44.1 | 0.521 | 49 | 0.535 | 48.6 | 0.76188 | 54 | 0.77675 | 55.8 | 1.0291 | 62 | 1.0434 | 60.3 | 1.6054 | 67 | 1.6184 | 69.3 | 2.2077 | 77 | 2.2247
35.1 | 0.062 | 39 | 0.079 | 36.9 | 0.128 | 41 | 0.143 | 40.5 | 0.154 | 45 | 0.169 | 42.3 | 0.285 | 47 | 0.3 | 45 | 0.499 | 50 | 0.512 | 49.5 | 0.7302 | 55 | 0.74342 | 56.7 | 0.98878 | 63 | 1.0018 | 61.2 | 1.5435 | 68 | 1.558 | 70.2 | 2.1257 | 78 | 2.1413
36 | 0.059 | 40 | 0.078 | 37.8 | 0.122 | 42 | 0.14 | 41.4 | 0.148 | 46 | 0.165 | 43.2 | 0.273 | 48 | 0.287 | 45.9 | 0.478 | 51 | 0.491 | 50.4 | 0.70058 | 56 | 0.71634 | 57.6 | 0.95099 | 64 | 0.96634 | 62.1 | 1.4853 | 69 | 1.4997 | 71.1 | 2.0488 | 79 | 2.0622
36.9 | 0.057 | 41 | 0.076 | 38.7 | 0.117 | 43 | 0.133 | 42.3 | 0.142 | 47 | 0.158 | 44.1 | 0.261 | 49 | 0.275 | 46.8 | 0.458 | 52 | 0.475 | 51.3 | 0.67279 | 57 | 0.68717 | 58.5 | 0.91544 | 65 | 0.92884 | 63 | 1.4306 | 70 | 1.4434 | 72 | 1.9763 | 80 | 1.9913
37.8 | 0.055 | 42 | 0.073 | 39.6 | 0.112 | 44 | 0.127 | 43.2 | 0.136 | 48 | 0.151 | 45 | 0.251 | 50 | 0.266 | 47.7 | 0.44 | 53 | 0.454 | 52.2 | 0.64674 | 58 | 0.66009 | 59.4 | 0.88202 | 66 | 0.8955 | 63.9 | 1.3792 | 71 | 1.3934 | 72.9 | 1.908 | 81 | 1.9247
38.7 | 0.052 | 43 | 0.073 | 40.5 | 0.108 | 45 | 0.125 | 44.1 | 0.13 | 49 | 0.148 | 45.9 | 0.241 | 51 | 0.258 | 48.6 | 0.422 | 54 | 0.435 | 53.1 | 0.62226 | 59 | 0.63509 | 60.3 | 0.8505 | 67 | 0.86634 | 64.8 | 1.3307 | 72 | 1.3434 | 73.8 | 1.8435 | 82 | 1.858
39.6 | 0.05 | 44 | 0.07 | 41.4 | 0.103 | 46 | 0.118 | 45 | 0.125 | 50 | 0.141 | 46.8 | 0.231 | 52 | 0.246 | 49.5 | 0.406 | 55 | 0.421 | 54 | 0.59921 | 60 | 0.61634 | 61.2 | 0.82075 | 68 | 0.83509 | 65.7 | 1.2849 | 73 | 1.2997 | 74.7 | 1.7826 | 83 | 1.7997
40.5 | 0.049 | 45 | 0.069 | 42.3 | 0.099 | 47 | 0.116 | 45.9 | 0.121 | 51 | 0.136 | 47.7 | 0.222 | 53 | 0.235 | 50.4 | 0.391 | 56 | 0.408 | 54.9 | 0.57749 | 61 | 0.59134 | 62.1 | 0.79266 | 69 | 0.808 | 66.6 | 1.2416 | 74 | 1.258 | 75.6 | 1.7249 | 84 | 1.7413
41.4 | 0.047 | 46 | 0.069 | 43.2 | 0.095 | 48 | 0.11 | 46.8 | 0.116 | 52 | 0.133 | 48.6 | 0.214 | 54 | 0.229 | 51.3 | 0.376 | 57 | 0.391 | 55.8 | 0.55699 | 62 | 0.5705 | 63 | 0.76606 | 70 | 0.783 | 67.5 | 1.2006 | 75 | 1.2163 | 76.5 | 1.6702 | 85 | 1.6851
42.3 | 0.045 | 47 | 0.068 | 44.1 | 0.092 | 49 | 0.108 | 47.7 | 0.112 | 53 | 0.127 | 49.5 | 0.206 | 55 | 0.221 | 52.2 | 0.363 | 58 | 0.377 | 56.7 | 0.5376 | 63 | 0.55175 | 63.9 | 0.7409 | 71 | 0.758 | 68.4 | 1.1617 | 76 | 1.1768 | 77.4 | 1.6183 | 86 | 1.633
43.2 | 0.044 | 48 | 0.066 | 45 | 0.089 | 50 | 0.102 | 48.6 | 0.108 | 54 | 0.125 | 50.4 | 0.199 | 56 | 0.216 | 53.1 | 0.35 | 59 | 0.366 | 57.6 | 0.51927 | 64 | 0.533 | 64.8 | 0.71699 | 72 | 0.733 | 69.3 | 1.1248 | 77 | 1.1413 | 78.3 | 1.569 | 87 | 1.583
44.1 | 0.042 | 49 | 0.065 | 45.9 | 0.085 | 51 | 0.101 | 49.5 | 0.104 | 55 | 0.119 | 51.3 | 0.192 | 57 | 0.208 | 54 | 0.338 | 60 | 0.352 | 58.5 | 0.50189 | 65 | 0.51634 | 65.7 | 0.69432 | 73 | 0.708 | 70.2 | 1.0898 | 78 | 1.1038 | 79.2 | 1.5221 | 88 | 1.5351
104.4 | 0.036 | 50 | 0.065 | 46.8 | 0.082 | 52 | 0.1 | 50.4 | 0.101 | 56 | 0.116 | 52.2 | 0.185 | 58 | 0.201 | 54.9 | 0.327 | 61 | 0.341 | 59.4 | 0.48545 | 66 | 0.49967 | 66.6 | 0.67278 | 74 | 0.68717 | 71.1 | 1.0565 | 79 | 1.0705 | 80.1 | 1.4775 | 89 | 1.4913
250.2 | 0.034 | 51 | 0.064 | 47.7 | 0.08 | 53 | 0.094 | 51.3 | 0.098 | 57 | 0.115 | 53.1 | 0.179 | 59 | 0.193 | 55.8 | 0.316 | 62 | 0.333 | 60.3 | 0.46979 | 67 | 0.48509 | 67.5 | 0.65229 | 75 | 0.66634 | 72 | 1.0248 | 80 | 1.0413 | 81 | 1.4349 | 90 | 1.4497
250.2 | 0.007 | 52 | 0.062 | 48.6 | 0.077 | 54 | 0.093 | 52.2 | 0.095 | 58 | 0.11 | 54 | 0.173 | 60 | 0.19 | 56.7 | 0.305 | 63 | 0.318 | 61.2 | 0.45495 | 68 | 0.46842 | 68.4 | 0.63275 | 76 | 0.64967 | 72.9 | 0.99457 | 81 | 1.008 | 81.9 | 1.3944 | 91 | 1.408
468 | 0.003 | 53 | 0.062 | 49.5 | 0.075 | 55 | 0.091 | 53.1 | 0.092 | 59 | 0.108 | 54.9 | 0.167 | 61 | 0.183 | 57.6 | 0.296 | 64 | 0.31 | 62.1 | 0.44085 | 69 | 0.458 | 69.3 | 0.61414 | 77 | 0.62675 | 73.8 | 0.96578 | 82 | 0.983 | 82.8 | 1.3556 | 92 | 1.3684
6300 | 0.003 | 54 | 0.061 | 50.4 | 0.072 | 56 | 0.09 | 54 | 0.089 | 60 | 0.106 | 55.8 | 0.162 | 62 | 0.177 | 58.5 | 0.286 | 65 | 0.3 | 63 | 0.4274 | 70 | 0.44134 | 70.2 | 0.59636 | 78 | 0.61009 | 74.7 | 0.93831 | 83 | 0.95175 | 83.7 | 1.3186 | 93 | 1.333
|  | 55 | 0.06 | 51.3 | 0.07 | 57 | 0.085 | 54.9 | 0.086 | 61 | 0.101 | 56.7 | 0.157 | 63 | 0.175 | 59.4 | 0.277 | 66 | 0.291 | 63.9 | 0.41462 | 71 | 0.42884 | 71.1 | 0.57943 | 79 | 0.59342 | 75.6 | 0.91205 | 84 | 0.92675 | 84.6 | 1.2832 | 94 | 1.2997
|  | 56 | 0.059 | 52.2 | 0.068 | 58 | 0.083 | 55.8 | 0.084 | 62 | 0.1 | 57.6 | 0.152 | 64 | 0.168 | 60.3 | 0.269 | 67 | 0.283 | 64.8 | 0.40241 | 72 | 0.41634 | 72 | 0.56322 | 80 | 0.57675 | 76.5 | 0.88696 | 85 | 0.90175 | 85.5 | 1.2493 | 95 | 1.2663
|  | 57 | 0.058 | 53.1 | 0.066 | 59 | 0.083 | 56.7 | 0.081 | 63 | 0.098 | 58.5 | 0.148 | 65 | 0.165 | 61.2 | 0.261 | 68 | 0.275 | 65.7 | 0.39077 | 73 | 0.408 | 72.9 | 0.54772 | 81 | 0.56217 | 77.4 | 0.86293 | 86 | 0.87675 | 86.4 | 1.2168 | 96 | 1.233
|  | 58 | 0.058 | 54 | 0.064 | 60 | 0.082 | 57.6 | 0.079 | 64 | 0.093 | 59.4 | 0.143 | 66 | 0.159 | 62.1 | 0.253 | 69 | 0.268 | 66.6 | 0.37966 | 74 | 0.39342 | 73.8 | 0.53289 | 82 | 0.54967 | 78.3 | 0.8399 | 87 | 0.85384 | 87.3 | 1.1857 | 97 | 1.1997
|  | 59 | 0.058 | 54.9 | 0.062 | 61 | 0.077 | 58.5 | 0.077 | 65 | 0.093 | 60.3 | 0.139 | 67 | 0.157 | 63 | 0.246 | 70 | 0.26 | 67.5 | 0.36904 | 75 | 0.383 | 74.7 | 0.5187 | 83 | 0.533 | 79.2 | 0.8179 | 88 | 0.833 | 88.2 | 1.1558 | 98 | 1.1684
|  | 60 | 0.057 | 55.8 | 0.06 | 62 | 0.076 | 59.4 | 0.075 | 66 | 0.091 | 61.2 | 0.135 | 68 | 0.151 | 63.9 | 0.239 | 71 | 0.254 | 68.4 | 0.35886 | 76 | 0.37467 | 75.6 | 0.50509 | 84 | 0.51842 | 80.1 | 0.79677 | 89 | 0.81009 | 89.1 | 1.1271 | 99 | 1.1413
|  | 61 | 0.057 | 56.7 | 0.059 | 63 | 0.075 | 60.3 | 0.073 | 67 | 0.09 | 62.1 | 0.132 | 69 | 0.148 | 64.8 | 0.232 | 72 | 0.25 | 69.3 | 0.34914 | 77 | 0.36634 | 76.5 | 0.49206 | 85 | 0.508 | 81 | 0.77649 | 90 | 0.79134 | 90 | 1.0995 | 100 | 1.1163
|  | 62 | 0.057 | 57.6 | 0.057 | 64 | 0.075 | 61.2 | 0.071 | 68 | 0.085 | 63 | 0.128 | 70 | 0.143 | 65.7 | 0.226 | 73 | 0.241 | 70.2 | 0.33979 | 78 | 0.35384 | 77.4 | 0.47952 | 86 | 0.49342 | 81.9 | 0.75707 | 91 | 0.7705 | 90.9 | 1.0731 | 101 | 1.0872
|  | 63 | 0.057 | 58.5 | 0.056 | 65 | 0.073 | 62.1 | 0.069 | 69 | 0.084 | 63.9 | 0.125 | 71 | 0.141 | 66.6 | 0.22 | 74 | 0.235 | 71.1 | 0.33087 | 79 | 0.3455 | 78.3 | 0.46746 | 87 | 0.483 | 82.8 | 0.73834 | 92 | 0.75175 | 91.8 | 1.0476 | 102 | 1.0622
|  | 64 | 0.057 | 59.4 | 0.054 | 66 | 0.069 | 63 | 0.067 | 70 | 0.083 | 64.8 | 0.121 | 72 | 0.136 | 67.5 | 0.214 | 75 | 0.229 | 72 | 0.3223 | 80 | 0.33509 | 79.2 | 0.45593 | 88 | 0.4705 | 83.7 | 0.72037 | 93 | 0.73509 | 92.7 | 1.0231 | 103 | 1.0372
|  | 65 | 0.057 | 60.3 | 0.053 | 67 | 0.068 | 63.9 | 0.066 | 71 | 0.083 | 65.7 | 0.118 | 73 | 0.134 | 68.4 | 0.209 | 76 | 0.225 | 72.9 | 0.31405 | 81 | 0.32675 | 80.1 | 0.44483 | 89 | 0.46009 | 84.6 | 0.70309 | 94 | 0.71842 | 93.6 | 0.99947 | 104 | 1.0163
|  | 66 | 0.057 | 61.2 | 0.052 | 68 | 0.068 | 64.8 | 0.064 | 72 | 0.082 | 66.6 | 0.115 | 74 | 0.132 | 69.3 | 0.203 | 77 | 0.218 | 73.8 | 0.30616 | 82 | 0.3205 | 81 | 0.43414 | 90 | 0.44967 | 85.5 | 0.68644 | 95 | 0.70175 | 94.5 | 0.97674 | 105 | 0.99134
|  | 67 | 0.057 | 62.1 | 0.051 | 69 | 0.066 | 65.7 | 0.062 | 73 | 0.078 | 67.5 | 0.112 | 75 | 0.127 | 70.2 | 0.198 | 78 | 0.212 | 74.7 | 0.29858 | 83 | 0.31217 | 81.9 | 0.4239 | 91 | 0.43717 | 86.4 | 0.6704 | 96 | 0.68509 | 95.4 | 0.95482 | 106 | 0.96842
|  | 68 | 0.057 | 63 | 0.049 | 70 | 0.066 | 66.6 | 0.061 | 74 | 0.076 | 68.4 | 0.109 | 76 | 0.125 | 71.1 | 0.193 | 79 | 0.208 | 75.6 | 0.29129 | 84 | 0.308 | 82.8 | 0.41397 | 92 | 0.42675 | 87.3 | 0.65496 | 97 | 0.66842 | 96.3 | 0.93368 | 107 | 0.94967
|  | 69 | 0.057 | 63.9 | 0.048 | 71 | 0.065 | 67.5 | 0.06 | 75 | 0.075 | 69.3 | 0.107 | 77 | 0.123 | 72 | 0.188 | 80 | 0.202 | 76.5 | 0.28428 | 85 | 0.29967 | 83.7 | 0.40444 | 93 | 0.41842 | 88.2 | 0.64008 | 98 | 0.65384 | 97.2 | 0.91326 | 108 | 0.92675
|  | 70 | 0.057 | 64.8 | 0.047 | 72 | 0.065 | 68.4 | 0.058 | 76 | 0.075 | 70.2 | 0.104 | 78 | 0.119 | 72.9 | 0.183 | 81 | 0.2 | 77.4 | 0.27751 | 86 | 0.29134 | 84.6 | 0.39525 | 94 | 0.41009 | 89.1 | 0.62572 | 99 | 0.64134 | 98.1 | 0.89358 | 109 | 0.908
|  | 71 | 0.056 | 65.7 | 0.046 | 73 | 0.061 | 69.3 | 0.057 | 77 | 0.073 | 71.1 | 0.102 | 79 | 0.118 | 73.8 | 0.179 | 82 | 0.193 | 78.3 | 0.27099 | 87 | 0.28509 | 85.5 | 0.38637 | 95 | 0.39967 | 90 | 0.61184 | 100 | 0.62675 | 99 | 0.87454 | 110 | 0.89134
|  | 500 | 0.048 | 66.6 | 0.045 | 500 | 0.048 | 70.2 | 0.056 | 78 | 0.073 | 72 | 0.099 | 80 | 0.116 | 74.7 | 0.175 | 83 | 0.191 | 79.2 | 0.26474 | 88 | 0.27884 | 86.4 | 0.3778 | 96 | 0.39134 | 90.9 | 0.59848 | 101 | 0.61217 | 99.9 | 0.85615 | 111 | 0.8705
|  | 500 | 0.033 | 67.5 | 0.044 | 500 | 0.033 | 71.1 | 0.054 | 79 | 0.069 | 72.9 | 0.097 | 81 | 0.114 | 75.6 | 0.171 | 84 | 0.186 | 80.1 | 0.2587 | 89 | 0.27467 | 87.3 | 0.36954 | 97 | 0.383 | 91.8 | 0.58553 | 102 | 0.59967 | 100.8 | 0.83837 | 112 | 0.85175
|  | 1000 | 0.033 | 68.4 | 0.043 | 1000 | 0.033 | 72 | 0.053 | 80 | 0.068 | 73.8 | 0.095 | 82 | 0.11 | 76.5 | 0.167 | 85 | 0.183 | 81 | 0.25288 | 90 | 0.26634 | 88.2 | 0.36155 | 98 | 0.37675 | 92.7 | 0.57303 | 103 | 0.58717 | 101.7 | 0.82118 | 113 | 0.83509
|  | 6300 | 0.022 | 163.8 | 0.035 | 6300 | 0.022 | 72.9 | 0.052 | 81 | 0.068 | 74.7 | 0.093 | 83 | 0.108 | 77.4 | 0.163 | 86 | 0.177 | 81.9 | 0.2473 | 91 | 0.26009 | 89.1 | 0.35384 | 99 | 0.36842 | 93.6 | 0.56098 | 104 | 0.57467 | 102.6 | 0.80454 | 114 | 0.81842
|  |  |  | 250.2 | 0.035 |  |  | 73.8 | 0.051 | 82 | 0.066 | 75.6 | 0.091 | 84 | 0.108 | 78.3 | 0.159 | 87 | 0.175 | 82.8 | 0.24186 | 92 | 0.258 | 90 | 0.34638 | 100 | 0.36009 | 94.5 | 0.54931 | 105 | 0.56634 | 103.5 | 0.78842 | 115 | 0.80175
|  |  |  | 250.2 | 0.007 |  |  | 74.7 | 0.05 | 83 | 0.066 | 76.5 | 0.089 | 85 | 0.106 | 79.2 | 0.156 | 88 | 0.173 | 83.7 | 0.23662 | 93 | 0.25175 | 90.9 | 0.33917 | 101 | 0.35384 | 95.4 | 0.53802 | 106 | 0.55175 | 104.4 | 0.77281 | 116 | 0.78717
|  |  |  | 468 | 0.003 |  |  | 75.6 | 0.049 | 84 | 0.066 | 77.4 | 0.087 | 86 | 0.102 | 80.1 | 0.153 | 89 | 0.168 | 84.6 | 0.23157 | 94 | 0.2455 | 91.8 | 0.33216 | 102 | 0.3455 | 96.3 | 0.5271 | 107 | 0.54134 | 105.3 | 0.75769 | 117 | 0.77467
|  |  |  | 6300 | 0.003 |  |  | 76.5 | 0.048 | 85 | 0.065 | 78.3 | 0.085 | 87 | 0.101 | 81 | 0.149 | 90 | 0.166 | 85.5 | 0.22667 | 95 | 0.24134 | 92.7 | 0.32542 | 103 | 0.34134 | 97.2 | 0.51651 | 108 | 0.533 | 106.2 | 0.74303 | 118 | 0.758
[8 empty] | 77.4 | 0.047 | 86 | 0.065 | 79.2 | 0.083 | 88 | 0.1 | 81.9 | 0.146 | 91 | 0.161 | 86.4 | 0.22194 | 96 | 0.23509 | 93.6 | 0.31888 | 104 | 0.333 | 98.1 | 0.50626 | 109 | 0.5205 | 107.1 | 0.72881 | 119 | 0.74342
[8 empty] | 78.3 | 0.046 | 87 | 0.061 | 80.1 | 0.082 | 89 | 0.098 | 82.8 | 0.143 | 92 | 0.159 | 87.3 | 0.21737 | 97 | 0.233 | 94.5 | 0.31256 | 105 | 0.32675 | 99 | 0.49632 | 110 | 0.51009 | 108 | 0.71504 | 120 | 0.72884
[8 empty] | 79.2 | 0.046 | 88 | 0.06 | 81 | 0.08 | 90 | 0.094 | 83.7 | 0.14 | 93 | 0.157 | 88.2 | 0.21295 | 98 | 0.22675 | 95.4 | 0.30643 | 106 | 0.3205 | 99.9 | 0.4867 | 111 | 0.50175 | 108.9 | 0.70165 | 121 | 0.71634
[8 empty] | 80.1 | 0.045 | 89 | 0.06 | 81.9 | 0.078 | 91 | 0.093 | 84.6 | 0.137 | 94 | 0.152 | 89.1 | 0.20867 | 99 | 0.22467 | 96.3 | 0.30049 | 107 | 0.31634 | 100.8 | 0.47735 | 112 | 0.49134 | 109.8 | 0.68866 | 122 | 0.70175
[8 empty] | 81 | 0.044 | 90 | 0.059 | 82.8 | 0.077 | 92 | 0.093 | 85.5 | 0.135 | 95 | 0.15 | 90 | 0.20451 | 100 | 0.21842 | 97.2 | 0.29472 | 108 | 0.308 | 101.7 | 0.46831 | 113 | 0.483 | 110.7 | 0.67607 | 123 | 0.69134
[8 empty] | 81.9 | 0.043 | 91 | 0.059 | 83.7 | 0.075 | 93 | 0.091 | 86.4 | 0.132 | 96 | 0.148 | 90.9 | 0.20049 | 101 | 0.21634 | 98.1 | 0.28913 | 109 | 0.30384 | 102.6 | 0.45952 | 114 | 0.47467 | 111.6 | 0.66385 | 124 | 0.67675
[8 empty] | 82.8 | 0.042 | 92 | 0.058 | 84.6 | 0.074 | 94 | 0.091 | 87.3 | 0.129 | 97 | 0.144 | 91.8 | 0.19658 | 102 | 0.21009 | 99 | 0.28371 | 110 | 0.29967 | 103.5 | 0.45097 | 115 | 0.46634 | 112.5 | 0.65194 | 125 | 0.66634
[8 empty] | 83.7 | 0.042 | 500 | 0.048 | 85.5 | 0.073 | 95 | 0.09 | 88.2 | 0.127 | 98 | 0.143 | 92.7 | 0.19253 | 103 | 0.208 | 99.9 | 0.27844 | 111 | 0.29342 | 104.4 | 0.44268 | 116 | 0.458 | 113.4 | 0.64038 | 126 | 0.65384
[8 empty] | 250.2 | 0.035 | 500 | 0.033 | 86.4 | 0.071 | 96 | 0.086 | 89.1 | 0.124 | 99 | 0.141 | 93.6 | 0.18887 | 104 | 0.20592 | 100.8 | 0.27333 | 112 | 0.28717 | 105.3 | 0.43463 | 117 | 0.44967 | 114.3 | 0.62914 | 127 | 0.64342
[8 empty] | 250.2 | 0.007 | 1000 | 0.033 | 87.3 | 0.07 | 97 | 0.085 | 90 | 0.122 | 100 | 0.136 | 94.5 | 0.18531 | 105 | 0.20106 | 101.7 | 0.26839 | 113 | 0.283 | 106.2 | 0.4268 | 118 | 0.44134 | 115.2 | 0.61821 | 128 | 0.633
[8 empty] | 468 | 0.003 | 6300 | 0.022 | 88.2 | 0.069 | 98 | 0.084 | 90.9 | 0.12 | 101 | 0.135 | 95.4 | 0.18187 | 106 | 0.19967 | 102.6 | 0.26356 | 114 | 0.27675 | 107.1 | 0.41919 | 119 | 0.433 | 116.1 | 0.60758 | 129 | 0.62467
[8 empty] | 6300 | 0.003 |  |  | 89.1 | 0.068 | 99 | 0.083 | 91.8 | 0.117 | 102 | 0.133 | 96.3 | 0.17854 | 107 | 0.19342 | 103.5 | 0.25887 | 115 | 0.27467 | 108 | 0.41181 | 120 | 0.42675 | 117 | 0.59724 | 130 | 0.61009
[12 empty] | 90 | 0.066 | 100 | 0.083 | 92.7 | 0.115 | 103 | 0.133 | 97.2 | 0.17528 | 108 | 0.19134 | 104.4 | 0.25431 | 116 | 0.26842 | 108.9 | 0.40461 | 121 | 0.41842 | 117.9 | 0.58716 | 131 | 0.60175
[12 empty] | 90.9 | 0.065 | 101 | 0.082 | 93.6 | 0.113 | 104 | 0.127 | 98.1 | 0.17214 | 109 | 0.18925 | 105.3 | 0.24988 | 117 | 0.26634 | 109.8 | 0.39762 | 122 | 0.41217 | 118.8 | 0.57737 | 132 | 0.59134
[12 empty] | 91.8 | 0.064 | 102 | 0.082 | 94.5 | 0.111 | 105 | 0.127 | 99 | 0.16907 | 110 | 0.18439 | 106.2 | 0.24556 | 118 | 0.26009 | 110.7 | 0.39083 | 123 | 0.408 | 119.7 | 0.56782 | 133 | 0.583
[12 empty] | 92.7 | 0.063 | 103 | 0.078 | 95.4 | 0.109 | 106 | 0.125 | 99.9 | 0.16611 | 111 | 0.183 | 107.1 | 0.24137 | 119 | 0.258 | 111.6 | 0.38421 | 124 | 0.39967 | 120.6 | 0.55851 | 134 | 0.57467
[12 empty] | 93.6 | 0.062 | 104 | 0.077 | 96.3 | 0.107 | 107 | 0.125 | 100.8 | 0.1632 | 112 | 0.17745 | 108 | 0.2373 | 120 | 0.25175 | 112.5 | 0.37776 | 125 | 0.39134 | 121.5 | 0.54944 | 135 | 0.56634
[12 empty] | 94.5 | 0.061 | 105 | 0.076 | 97.2 | 0.105 | 108 | 0.123 | 101.7 | 0.16041 | 113 | 0.17606 | 108.9 | 0.23332 | 121 | 0.24967 | 113.4 | 0.37148 | 126 | 0.38509 | 122.4 | 0.54061 | 136 | 0.558
[12 empty] | 95.4 | 0.06 | 106 | 0.076 | 98.1 | 0.104 | 109 | 0.118 | 102.6 | 0.15766 | 114 | 0.17467 | 109.8 | 0.22945 | 122 | 0.24342 | 114.3 | 0.36536 | 127 | 0.37884 | 123.3 | 0.532 | 137 | 0.5455
[12 empty] | 96.3 | 0.059 | 107 | 0.075 | 99 | 0.102 | 110 | 0.118 | 103.5 | 0.15499 | 115 | 0.16911 | 110.7 | 0.2257 | 123 | 0.24134 | 115.2 | 0.35941 | 128 | 0.37467 | 124.2 | 0.52361 | 138 | 0.53717
[12 empty] | 97.2 | 0.058 | 108 | 0.075 | 99.9 | 0.1 | 111 | 0.116 | 104.4 | 0.15241 | 116 | 0.16773 | 111.6 | 0.22204 | 124 | 0.23509 | 116.1 | 0.3536 | 129 | 0.36842 | 125.1 | 0.51542 | 139 | 0.52884
[12 empty] | 98.1 | 0.057 | 109 | 0.075 | 100.8 | 0.099 | 112 | 0.116 | 105.3 | 0.14989 | 117 | 0.16634 | 112.5 | 0.21846 | 125 | 0.233 | 117 | 0.34795 | 130 | 0.36217 | 126 | 0.50741 | 140 | 0.52467
[12 empty] | 99 | 0.056 | 110 | 0.073 | 101.7 | 0.097 | 113 | 0.111 | 106.2 | 0.14746 | 118 | 0.16495 | 113.4 | 0.21497 | 126 | 0.22884 | 117.9 | 0.34242 | 131 | 0.358 | 126.9 | 0.49964 | 141 | 0.51634
[12 empty] | 99.9 | 0.055 | 111 | 0.069 | 102.6 | 0.095 | 114 | 0.11 | 107.1 | 0.14505 | 119 | 0.16009 | 114.3 | 0.21158 | 127 | 0.22675 | 118.8 | 0.33706 | 132 | 0.35175 | 127.8 | 0.49202 | 142 | 0.508
[12 empty] | 100.8 | 0.055 | 112 | 0.069 | 103.5 | 0.094 | 115 | 0.109 | 108 | 0.14274 | 120 | 0.158 | 115.2 | 0.20827 | 128 | 0.22467 | 119.7 | 0.33181 | 133 | 0.3455 | 128.7 | 0.48461 | 143 | 0.49967
[12 empty] | 101.7 | 0.054 | 113 | 0.068 | 104.4 | 0.092 | 116 | 0.108 | 108.9 | 0.14046 | 121 | 0.158 | 116.1 | 0.20504 | 129 | 0.21842 | 120.6 | 0.32667 | 134 | 0.34134 | 129.6 | 0.47734 | 144 | 0.49134
[12 empty] | 102.6 | 0.053 | 114 | 0.068 | 105.3 | 0.091 | 117 | 0.108 | 109.8 | 0.13825 | 122 | 0.15245 | 117 | 0.2019 | 130 | 0.21634 | 121.5 | 0.32167 | 135 | 0.33509 | 130.5 | 0.47027 | 145 | 0.48509
[12 empty] | 103.5 | 0.052 | 115 | 0.068 | 106.2 | 0.09 | 118 | 0.107 | 110.7 | 0.13607 | 123 | 0.15106 | 117.9 | 0.19882 | 131 | 0.21634 | 122.4 | 0.31679 | 136 | 0.333 | 131.4 | 0.46334 | 146 | 0.47675
[12 empty] | 104.4 | 0.051 | 116 | 0.068 | 107.1 | 0.088 | 119 | 0.102 | 111.6 | 0.13401 | 124 | 0.14967 | 118.8 | 0.19583 | 132 | 0.21009 | 123.3 | 0.31203 | 137 | 0.32675 | 132.3 | 0.4566 | 147 | 0.4705
[12 empty] | 105.3 | 0.051 | 117 | 0.066 | 108 | 0.087 | 120 | 0.102 | 112.5 | 0.13193 | 125 | 0.14967 | 119.7 | 0.19259 | 133 | 0.208 | 124.2 | 0.30739 | 138 | 0.32467 | 133.2 | 0.44998 | 148 | 0.46634
[12 empty] | 106.2 | 0.05 | 118 | 0.066 | 108.9 | 0.086 | 121 | 0.101 | 113.4 | 0.12994 | 126 | 0.14412 | 120.6 | 0.18975 | 134 | 0.20661 | 125.1 | 0.30284 | 139 | 0.31634 | 134.1 | 0.44354 | 149 | 0.458
[12 empty] | 107.1 | 0.049 | 119 | 0.066 | 109.8 | 0.084 | 122 | 0.1 | 114.3 | 0.12799 | 127 | 0.14342 | 121.5 | 0.18694 | 135 | 0.20175 | 126 | 0.29838 | 140 | 0.31217 | 135 | 0.43722 | 150 | 0.45175
[12 empty] | 108 | 0.049 | 120 | 0.066 | 110.7 | 0.083 | 123 | 0.1 | 115.2 | 0.12609 | 128 | 0.14134 | 122.4 | 0.18425 | 136 | 0.19967 | 126.9 | 0.29407 | 141 | 0.308 | 135.9 | 0.43106 | 151 | 0.4455
[12 empty] | 108.9 | 0.048 | 121 | 0.065 | 111.6 | 0.082 | 124 | 0.098 | 116.1 | 0.12423 | 129 | 0.14134 | 123.3 | 0.18156 | 137 | 0.19828 | 127.8 | 0.28981 | 142 | 0.30384 | 136.8 | 0.42502 | 152 | 0.44134
[12 empty] | 109.8 | 0.047 | 122 | 0.065 | 112.5 | 0.081 | 125 | 0.098 | 117 | 0.12243 | 130 | 0.13995 | 124.2 | 0.17897 | 138 | 0.19342 | 128.7 | 0.28569 | 143 | 0.29967 | 137.7 | 0.41912 | 153 | 0.433
[12 empty] | 110.7 | 0.047 | 123 | 0.061 | 113.4 | 0.079 | 126 | 0.094 | 117.9 | 0.12066 | 131 | 0.13508 | 125.1 | 0.17642 | 139 | 0.19273 | 129.6 | 0.28163 | 144 | 0.2955 | 138.6 | 0.41335 | 154 | 0.42675
[12 empty] | 111.6 | 0.046 | 124 | 0.061 | 114.3 | 0.078 | 127 | 0.093 | 118.8 | 0.11893 | 132 | 0.13439 | 126 | 0.17392 | 140 | 0.19134 | 130.5 | 0.27768 | 145 | 0.29134 | 139.5 | 0.40771 | 155 | 0.42467
[12 empty] | 112.5 | 0.046 | 125 | 0.06 | 115.2 | 0.077 | 128 | 0.093 | 119.7 | 0.11724 | 133 | 0.133 | 126.9 | 0.1715 | 141 | 0.18578 | 131.4 | 0.27379 | 146 | 0.28717 | 140.4 | 0.40216 | 156 | 0.41634
[12 empty] | 113.4 | 0.045 | 126 | 0.06 | 116.1 | 0.076 | 129 | 0.091 | 120.6 | 0.1156 | 134 | 0.133 | 127.8 | 0.16913 | 142 | 0.18439 | 132.3 | 0.27002 | 147 | 0.28509 | 141.3 | 0.39675 | 157 | 0.41009
[12 empty] | 114.3 | 0.044 | 127 | 0.06 | 117 | 0.075 | 130 | 0.091 | 121.5 | 0.11397 | 135 | 0.13162 | 128.7 | 0.16682 | 143 | 0.183 | 133.2 | 0.2663 | 148 | 0.283 | 142.2 | 0.39147 | 158 | 0.408
[12 empty] | 115.2 | 0.044 | 128 | 0.059 | 117.9 | 0.074 | 131 | 0.091 | 122.4 | 0.11243 | 136 | 0.12745 | 129.6 | 0.16454 | 144 | 0.18162 | 134.1 | 0.26269 | 149 | 0.27675 | 143.1 | 0.38629 | 159 | 0.39967
[12 empty] | 116.1 | 0.043 | 129 | 0.059 | 118.8 | 0.073 | 132 | 0.09 | 123.3 | 0.11087 | 137 | 0.12606 | 130.5 | 0.16232 | 145 | 0.17675 | 135 | 0.25914 | 150 | 0.27467 | 144 | 0.3812 | 160 | 0.3955
[12 empty] | 117 | 0.043 | 130 | 0.058 | 119.7 | 0.072 | 133 | 0.089 | 124.2 | 0.10938 | 138 | 0.12467 | 131.4 | 0.16013 | 146 | 0.17606 | 135.9 | 0.25567 | 151 | 0.26842 | 144.9 | 0.37622 | 161 | 0.39134
[12 empty] | 117.9 | 0.042 | 500 | 0.048 | 120.6 | 0.071 | 134 | 0.086 | 125.1 | 0.1079 | 139 | 0.12467 | 132.3 | 0.15801 | 147 | 0.17467 | 136.8 | 0.25226 | 152 | 0.26634 | 145.8 | 0.37135 | 162 | 0.38509
[12 empty] | 250.2 | 0.036 | 500 | 0.033 | 121.5 | 0.07 | 135 | 0.085 | 126 | 0.10645 | 140 | 0.12328 | 133.2 | 0.15593 | 148 | 0.17328 | 137.7 | 0.24894 | 153 | 0.26634 | 146.7 | 0.36657 | 163 | 0.383
[12 empty] | 250.2 | 0.007 | 1000 | 0.033 | 122.4 | 0.069 | 136 | 0.084 | 126.9 | 0.10504 | 141 | 0.11911 | 134.1 | 0.15389 | 149 | 0.16842 | 138.6 | 0.24568 | 154 | 0.26009 | 147.6 | 0.36189 | 164 | 0.37675
[12 empty] | 468 | 0.003 | 6300 | 0.022 | 123.3 | 0.068 | 137 | 0.084 | 127.8 | 0.10367 | 142 | 0.11841 | 135 | 0.15189 | 150 | 0.16773 | 139.5 | 0.24249 | 155 | 0.258 | 148.5 | 0.35731 | 165 | 0.37467
[12 empty] | 6300 | 0.003 |  |  | 124.2 | 0.068 | 138 | 0.083 | 128.7 | 0.10233 | 143 | 0.11772 | 135.9 | 0.14994 | 151 | 0.16634 | 140.4 | 0.23935 | 156 | 0.25384 | 149.4 | 0.35284 | 166 | 0.36634
[16 empty] | 125.1 | 0.067 | 139 | 0.083 | 129.6 | 0.10101 | 144 | 0.11634 | 136.8 | 0.14801 | 152 | 0.16495 | 141.3 | 0.23629 | 157 | 0.24967 | 150.3 | 0.34843 | 167 | 0.36217
[16 empty] | 126 | 0.066 | 140 | 0.083 | 130.5 | 0.099723 | 145 | 0.11634 | 137.7 | 0.14616 | 153 | 0.16078 | 142.2 | 0.23331 | 158 | 0.24967 | 151.2 | 0.34412 | 168 | 0.358
[16 empty] | 126.9 | 0.065 | 141 | 0.082 | 131.4 | 0.098445 | 146 | 0.11496 | 138.6 | 0.14431 | 154 | 0.15939 | 143.1 | 0.23036 | 159 | 0.24342 | 152.1 | 0.33987 | 169 | 0.35384
[16 empty] | 127.8 | 0.064 | 142 | 0.082 | 132.3 | 0.097213 | 147 | 0.11496 | 139.5 | 0.14252 | 155 | 0.158 | 144 | 0.22747 | 160 | 0.24134 | 153 | 0.33572 | 170 | 0.34967
[16 empty] | 128.7 | 0.064 | 143 | 0.078 | 133.2 | 0.096001 | 148 | 0.11079 | 140.4 | 0.14075 | 156 | 0.158 | 144.9 | 0.22464 | 161 | 0.24134 | 153.9 | 0.33164 | 171 | 0.3455
[16 empty] | 129.6 | 0.063 | 144 | 0.078 | 134.1 | 0.094813 | 149 | 0.1101 | 141.3 | 0.13903 | 157 | 0.15661 | 145.8 | 0.22186 | 162 | 0.23509 | 154.8 | 0.32765 | 172 | 0.34134
[16 empty] | 130.5 | 0.062 | 145 | 0.077 | 135 | 0.093647 | 150 | 0.1094 | 142.2 | 0.13731 | 158 | 0.15175 | 146.7 | 0.21915 | 163 | 0.233 | 155.7 | 0.32372 | 173 | 0.33717
[16 empty] | 131.4 | 0.061 | 146 | 0.077 | 135.9 | 0.092507 | 151 | 0.108 | 143.1 | 0.13567 | 159 | 0.15106 | 147.6 | 0.21648 | 164 | 0.233 | 156.6 | 0.31987 | 174 | 0.33509
[16 empty] | 132.3 | 0.061 | 147 | 0.076 | 136.8 | 0.091387 | 152 | 0.108 | 144 | 0.13404 | 160 | 0.14967 | 148.5 | 0.21387 | 165 | 0.22675 | 157.5 | 0.31609 | 175 | 0.333
[16 empty] | 133.2 | 0.06 | 148 | 0.076 | 137.7 | 0.09031 | 153 | 0.108 | 144.9 | 0.13245 | 161 | 0.14967 | 149.4 | 0.21132 | 166 | 0.22467 | 158.4 | 0.31239 | 176 | 0.32675
[16 empty] | 134.1 | 0.059 | 149 | 0.075 | 138.6 | 0.089225 | 154 | 0.1066 | 145.8 | 0.13088 | 162 | 0.14828 | 150.3 | 0.20881 | 167 | 0.22467 | 159.3 | 0.30875 | 177 | 0.32467
[16 empty] | 135 | 0.059 | 150 | 0.075 | 139.5 | 0.088185 | 155 | 0.10243 | 146.7 | 0.12933 | 163 | 0.14412 | 151.2 | 0.20635 | 168 | 0.2205 | 160.2 | 0.30518 | 178 | 0.31842
[16 empty] | 135.9 | 0.058 | 151 | 0.075 | 140.4 | 0.087157 | 156 | 0.10174 | 147.6 | 0.12782 | 164 | 0.14342 | 152.1 | 0.20392 | 169 | 0.21842 | 161.1 | 0.30167 | 179 | 0.31634
[16 empty] | 136.8 | 0.057 | 152 | 0.075 | 141.3 | 0.086154 | 157 | 0.10105 | 148.5 | 0.12634 | 165 | 0.14273 | 153 | 0.20155 | 170 | 0.21634 | 162 | 0.29824 | 180 | 0.31217
[16 empty] | 137.7 | 0.057 | 153 | 0.073 | 142.2 | 0.085144 | 158 | 0.10105 | 149.4 | 0.12489 | 166 | 0.14134 | 153.9 | 0.1992 | 171 | 0.21634 | 162.9 | 0.29484 | 181 | 0.31009
[16 empty] | 138.6 | 0.056 | 154 | 0.073 | 143.1 | 0.084185 | 159 | 0.099673 | 150.3 | 0.12346 | 167 | 0.13995 | 154.8 | 0.19692 | 172 | 0.21009 | 163.8 | 0.29154 | 182 | 0.308
[16 empty] | 139.5 | 0.055 | 155 | 0.069 | 144 | 0.083235 | 160 | 0.099673 | 151.2 | 0.12207 | 168 | 0.13578 | 155.7 | 0.19466 | 173 | 0.208 | 164.7 | 0.28828 | 183 | 0.30175
[16 empty] | 140.4 | 0.055 | 156 | 0.069 | 144.9 | 0.082302 | 161 | 0.099673 | 152.1 | 0.1207 | 169 | 0.13508 | 156.6 | 0.19215 | 174 | 0.208 | 165.6 | 0.28506 | 184 | 0.29967
[16 empty] | 141.3 | 0.054 | 157 | 0.068 | 145.8 | 0.081388 | 162 | 0.098297 | 153 | 0.11936 | 170 | 0.13439 | 157.5 | 0.18998 | 175 | 0.20661 | 166.5 | 0.28191 | 185 | 0.2955
[16 empty] | 142.2 | 0.054 | 158 | 0.068 | 146.7 | 0.080478 | 163 | 0.097608 | 153.9 | 0.11803 | 171 | 0.13439 | 158.4 | 0.18786 | 176 | 0.20245 | 167.4 | 0.27882 | 186 | 0.29342
[16 empty] | 143.1 | 0.053 | 159 | 0.068 | 147.6 | 0.079594 | 164 | 0.09414 | 154.8 | 0.11673 | 172 | 0.133 | 159.3 | 0.18578 | 177 | 0.20106 | 168.3 | 0.27577 | 187 | 0.29134
[16 empty] | 144 | 0.052 | 160 | 0.068 | 148.5 | 0.078721 | 165 | 0.09344 | 155.7 | 0.11546 | 173 | 0.133 | 160.2 | 0.18373 | 178 | 0.19967 | 169.2 | 0.27279 | 188 | 0.28717
[16 empty] | 144.9 | 0.052 | 161 | 0.068 | 149.4 | 0.077876 | 166 | 0.09344 | 156.6 | 0.1142 | 174 | 0.13162 | 161.1 | 0.1817 | 179 | 0.19828 | 170.1 | 0.26986 | 189 | 0.28509
[16 empty] | 145.8 | 0.051 | 162 | 0.068 | 150.3 | 0.077032 | 167 | 0.092739 | 157.5 | 0.11297 | 175 | 0.12745 | 162 | 0.17972 | 180 | 0.19411 | 171 | 0.26695 | 190 | 0.283
[16 empty] | 146.7 | 0.051 | 163 | 0.066 | 151.2 | 0.076216 | 168 | 0.091333 | 158.4 | 0.11176 | 176 | 0.12676 | 162.9 | 0.17777 | 181 | 0.19273 | 171.9 | 0.26412 | 191 | 0.27884
[16 empty] | 147.6 | 0.05 | 164 | 0.066 | 152.1 | 0.075417 | 169 | 0.091332 | 159.3 | 0.11059 | 177 | 0.12606 | 163.8 | 0.17585 | 182 | 0.19134 | 172.8 | 0.26132 | 192 | 0.27467
[16 empty] | 148.5 | 0.05 | 165 | 0.066 | 153 | 0.074631 | 170 | 0.091333 | 160.2 | 0.10942 | 178 | 0.12467 | 164.7 | 0.17398 | 183 | 0.19134 | 173.7 | 0.25858 | 193 | 0.27467
[16 empty] | 149.4 | 0.049 | 166 | 0.066 | 153.9 | 0.07385 | 171 | 0.091332 | 161.1 | 0.10827 | 179 | 0.12467 | 165.6 | 0.17211 | 184 | 0.18925 | 174.6 | 0.25587 | 194 | 0.2705
[16 empty] | 150.3 | 0.049 | 167 | 0.066 | 154.8 | 0.073092 | 172 | 0.089925 | 162 | 0.10714 | 180 | 0.12467 | 166.5 | 0.17031 | 185 | 0.18509 | 175.5 | 0.25322 | 195 | 0.26842
[16 empty] | 151.2 | 0.048 | 168 | 0.065 | 155.7 | 0.07234 | 173 | 0.089925 | 162.9 | 0.10604 | 181 | 0.12328 | 167.4 | 0.16851 | 186 | 0.18439 | 176.4 | 0.2506 | 196 | 0.26634
[16 empty] | 152.1 | 0.048 | 169 | 0.065 | 156.6 | 0.071604 | 174 | 0.085744 | 163.8 | 0.10494 | 182 | 0.11911 | 168.3 | 0.16676 | 187 | 0.183 | 177.3 | 0.24805 | 197 | 0.26217
[16 empty] | 153 | 0.047 | 170 | 0.065 | 157.5 | 0.070873 | 175 | 0.085744 | 164.7 | 0.10388 | 183 | 0.11841 | 169.2 | 0.16502 | 188 | 0.18162 | 178.2 | 0.2455 | 198 | 0.26009
[16 empty] | 153.9 | 0.047 | 171 | 0.064 | 158.4 | 0.070167 | 176 | 0.085057 | 165.6 | 0.10281 | 184 | 0.11841 | 170.1 | 0.16332 | 189 | 0.17745 | 179.1 | 0.24302 | 199 | 0.258
[16 empty] | 154.8 | 0.047 | 172 | 0.061 | 159.3 | 0.069484 | 177 | 0.084373 | 166.5 | 0.10179 | 185 | 0.11772 | 171 | 0.16165 | 190 | 0.17675 | 180 | 0.24056 | 200 | 0.258
[16 empty] | 155.7 | 0.046 | 173 | 0.061 | 160.2 | 0.068799 | 178 | 0.084373 | 167.4 | 0.10076 | 186 | 0.11634 | 171.9 | 0.16 | 191 | 0.17606 | 180.9 | 0.23817 | 201 | 0.25175
[16 empty] | 156.6 | 0.046 | 174 | 0.061 | 161.1 | 0.068116 | 179 | 0.084373 | 168.3 | 0.099774 | 187 | 0.11634 | 172.8 | 0.15838 | 192 | 0.17467 | 181.8 | 0.23579 | 202 | 0.24967
[16 empty] | 157.5 | 0.045 | 175 | 0.06 | 162 | 0.067458 | 180 | 0.08301 | 169.2 | 0.098775 | 188 | 0.11634 | 173.7 | 0.15678 | 193 | 0.17328 | 182.7 | 0.23346 | 203 | 0.24967
[16 empty] | 158.4 | 0.045 | 176 | 0.06 | 162.9 | 0.066805 | 181 | 0.08301 | 170.1 | 0.097809 | 189 | 0.11496 | 174.6 | 0.15522 | 194 | 0.16911 | 183.6 | 0.23116 | 204 | 0.2455
[16 empty] | 159.3 | 0.044 | 177 | 0.06 | 163.8 | 0.066161 | 182 | 0.08301 | 171 | 0.09686 | 190 | 0.11079 | 175.5 | 0.15369 | 195 | 0.16842 | 184.5 | 0.2289 | 205 | 0.24342
[16 empty] | 160.2 | 0.044 | 178 | 0.059 | 164.7 | 0.065538 | 183 | 0.08301 | 171.9 | 0.09592 | 191 | 0.11079 | 176.4 | 0.15218 | 196 | 0.16773 | 185.4 | 0.22665 | 206 | 0.24134
[16 empty] | 161.1 | 0.044 | 179 | 0.059 | 165.6 | 0.064905 | 184 | 0.081649 | 172.8 | 0.094992 | 192 | 0.1101 | 177.3 | 0.15069 | 197 | 0.16634 | 186.3 | 0.22447 | 207 | 0.24134
[16 empty] | 162 | 0.043 | 180 | 0.059 | 166.5 | 0.064303 | 185 | 0.081649 | 173.7 | 0.094074 | 193 | 0.1094 | 178.2 | 0.14922 | 198 | 0.16634 | 187.2 | 0.22231 | 208 | 0.23509
[16 empty] | 162.9 | 0.043 | 181 | 0.059 | 167.4 | 0.063697 | 186 | 0.080966 | 174.6 | 0.09319 | 194 | 0.1094 | 179.1 | 0.14776 | 199 | 0.16495 | 188.1 | 0.22019 | 209 | 0.23509
[16 empty] | 163.8 | 0.043 | 182 | 0.058 | 168.3 | 0.06311 | 187 | 0.077503 | 175.5 | 0.092322 | 195 | 0.108 | 180 | 0.14633 | 200 | 0.16078 | 189 | 0.21808 | 210 | 0.233
[16 empty] | 164.7 | 0.042 | 500 | 0.05 | 169.2 | 0.062521 | 188 | 0.077503 | 176.4 | 0.091456 | 196 | 0.108 | 180.9 | 0.14494 | 201 | 0.16009 | 189.9 | 0.21602 | 211 | 0.233
[16 empty] | 165.6 | 0.042 | 500 | 0.033 | 170.1 | 0.061947 | 189 | 0.076797 | 177.3 | 0.090613 | 197 | 0.108 | 181.8 | 0.14355 | 202 | 0.15939 | 190.8 | 0.214 | 212 | 0.22675
[16 empty] | 166.5 | 0.042 | 1000 | 0.033 | 171 | 0.061388 | 190 | 0.076797 | 178.2 | 0.089765 | 198 | 0.1066 | 182.7 | 0.1422 | 203 | 0.158 | 191.7 | 0.212 | 213 | 0.22675
[16 empty] | 167.4 | 0.042 | 6300 | 0.022 | 171.9 | 0.060838 | 191 | 0.076088 | 179.1 | 0.088937 | 199 | 0.1066 | 183.6 | 0.14087 | 204 | 0.158 | 192.6 | 0.21002 | 214 | 0.22467
[16 empty] | 168.3 | 0.042 |  |  | 172.8 | 0.060291 | 192 | 0.076088 | 180 | 0.088125 | 200 | 0.10243 | 184.5 | 0.13954 | 205 | 0.15661 | 193.5 | 0.20807 | 215 | 0.22467
[16 empty] | 169.2 | 0.042 |  |  | 173.7 | 0.059745 | 193 | 0.076088 | 180.9 | 0.087333 | 201 | 0.10174 | 185.4 | 0.13824 | 206 | 0.15245 | 194.4 | 0.20616 | 216 | 0.2205
[16 empty] | 170.1 | 0.042 |  |  | 174.6 | 0.059231 | 194 | 0.07466 | 181.8 | 0.086537 | 202 | 0.10174 | 186.3 | 0.13696 | 207 | 0.15175 | 195.3 | 0.20427 | 217 | 0.21842
[16 empty] | 171 | 0.042 |  |  | 175.5 | 0.058724 | 195 | 0.074661 | 182.7 | 0.085763 | 203 | 0.10105 | 187.2 | 0.1357 | 208 | 0.15106 | 196.2 | 0.20241 | 218 | 0.21634
[16 empty] | 171.9 | 0.042 |  |  | 176.4 | 0.058209 | 196 | 0.074661 | 183.6 | 0.085009 | 204 | 0.10105 | 188.1 | 0.13446 | 209 | 0.14967 | 197.1 | 0.20057 | 219 | 0.21634
[16 empty] | 172.8 | 0.042 |  |  | 177.3 | 0.057716 | 197 | 0.074661 | 184.5 | 0.084241 | 205 | 0.099673 | 189 | 0.13323 | 210 | 0.14967 | 198 | 0.19877 | 220 | 0.21217
[16 empty] | 173.7 | 0.042 |  |  | 178.2 | 0.05721 | 198 | 0.07466 | 185.4 | 0.083499 | 206 | 0.099673 | 189.9 | 0.13204 | 211 | 0.14967 | 198.9 | 0.197 | 221 | 0.21009
[16 empty] | 174.6 | 0.042 |  |  | 179.1 | 0.056722 | 199 | 0.073231 | 186.3 | 0.082763 | 207 | 0.099673 | 190.8 | 0.13084 | 212 | 0.14828 | 199.8 | 0.19524 | 222 | 0.21009
[16 empty] | 175.5 | 0.041 |  |  | 180 | 0.05624 | 200 | 0.073231 | 187.2 | 0.082056 | 208 | 0.099673 | 191.7 | 0.12968 | 213 | 0.14412 | 200.7 | 0.19322 | 223 | 0.20939
[16 empty] | 176.4 | 0.041 |  |  | 180.9 | 0.05577 | 201 | 0.07323 | 188.1 | 0.081347 | 209 | 0.098297 | 192.6 | 0.12851 | 214 | 0.14342 | 201.6 | 0.1915 | 224 | 0.208
[16 empty] | 177.3 | 0.041 |  |  | 181.8 | 0.055304 | 202 | 0.069033 | 189 | 0.080636 | 210 | 0.098297 | 193.5 | 0.12738 | 215 | 0.14273 | 202.5 | 0.18983 | 225 | 0.20661
[16 empty] | 178.2 | 0.041 |  |  | 182.7 | 0.054842 | 203 | 0.069033 | 189.9 | 0.079953 | 211 | 0.09414 | 194.4 | 0.12625 | 216 | 0.14134 | 203.4 | 0.18817 | 226 | 0.20245
[16 empty] | 179.1 | 0.041 |  |  | 183.6 | 0.054398 | 204 | 0.069033 | 190.8 | 0.079264 | 212 | 0.09414 | 195.3 | 0.12515 | 217 | 0.14134 | 204.3 | 0.18653 | 227 | 0.20175
[16 empty] | 180 | 0.041 |  |  | 184.5 | 0.053949 | 205 | 0.068355 | 191.7 | 0.07861 | 213 | 0.09344 | 196.2 | 0.12406 | 218 | 0.14134 | 205.2 | 0.18492 | 228 | 0.20106
[16 empty] | 180.9 | 0.041 |  |  | 185.4 | 0.053508 | 206 | 0.068355 | 192.6 | 0.07794 | 214 | 0.09344 | 197.1 | 0.123 | 219 | 0.13995 | 206.1 | 0.18332 | 229 | 0.19967
[16 empty] | 181.8 | 0.041 |  |  | 186.3 | 0.053073 | 207 | 0.068355 | 193.5 | 0.077292 | 215 | 0.092739 | 198 | 0.12192 | 220 | 0.13578 | 207 | 0.18175 | 230 | 0.19828
[16 empty] | 182.7 | 0.041 |  |  | 187.2 | 0.052649 | 208 | 0.067683 | 194.4 | 0.076642 | 216 | 0.092739 | 198.9 | 0.12089 | 221 | 0.13578 | 207.9 | 0.18021 | 231 | 0.19411
[16 empty] | 183.6 | 0.041 |  |  | 188.1 | 0.05223 | 209 | 0.067683 | 195.3 | 0.076012 | 217 | 0.091332 | 199.8 | 0.11986 | 222 | 0.13508 | 208.8 | 0.17868 | 232 | 0.19342
[16 empty] | 184.5 | 0.041 |  |  | 189 | 0.051809 | 210 | 0.067683 | 196.2 | 0.075394 | 218 | 0.091332 | 200.7 | 0.11885 | 223 | 0.13439 | 209.7 | 0.17717 | 233 | 0.19273
[16 empty] | 185.4 | 0.041 |  |  | 189.9 | 0.051406 | 211 | 0.066351 | 197.1 | 0.074782 | 219 | 0.091333 | 201.6 | 0.11784 | 224 | 0.133 | 210.6 | 0.17569 | 234 | 0.19134
[16 empty] | 186.3 | 0.041 |  |  | 190.8 | 0.050997 | 212 | 0.066351 | 198 | 0.074167 | 220 | 0.091333 | 202.5 | 0.11686 | 225 | 0.133 | 211.5 | 0.17421 | 235 | 0.19134
[16 empty] | 187.2 | 0.041 |  |  | 191.7 | 0.050605 | 213 | 0.066351 | 198.9 | 0.073578 | 221 | 0.091332 | 203.4 | 0.11588 | 226 | 0.133 | 212.4 | 0.17279 | 236 | 0.18995
[16 empty] | 188.1 | 0.041 |  |  | 192.6 | 0.050206 | 214 | 0.066351 | 199.8 | 0.072983 | 222 | 0.089925 | 204.3 | 0.11492 | 227 | 0.13162 | 213.3 | 0.17135 | 237 | 0.18578
[16 empty] | 189 | 0.041 |  |  | 193.5 | 0.049827 | 215 | 0.066351 | 200.7 | 0.0724 | 223 | 0.089925 | 205.2 | 0.11397 | 228 | 0.13162 | 214.2 | 0.16994 | 238 | 0.18509
[16 empty] | 189.9 | 0.041 |  |  | 194.4 | 0.049438 | 216 | 0.066351 | 201.6 | 0.071822 | 224 | 0.085744 | 206.1 | 0.11304 | 229 | 0.12745 | 215.1 | 0.16855 | 239 | 0.18439
[16 empty] | 190.8 | 0.041 |  |  | 195.3 | 0.04906 | 217 | 0.066351 | 202.5 | 0.071267 | 225 | 0.085744 | 207 | 0.11212 | 230 | 0.12676 | 216 | 0.16718 | 240 | 0.183
[16 empty] | 191.7 | 0.041 |  |  | 196.2 | 0.048701 | 218 | 0.066351 | 203.4 | 0.070706 | 226 | 0.085057 | 207.9 | 0.1112 | 231 | 0.12676 | 216.9 | 0.16582 | 241 | 0.183
[16 empty] | 192.6 | 0.041 |  |  | 197.1 | 0.04834 | 219 | 0.065023 | 204.3 | 0.070145 | 227 | 0.085057 | 208.8 | 0.11031 | 232 | 0.12606 | 217.8 | 0.16448 | 242 | 0.18162
[16 empty] | 193.5 | 0.041 |  |  | 198 | 0.047965 | 220 | 0.065023 | 205.2 | 0.06961 | 228 | 0.085057 | 209.7 | 0.10941 | 233 | 0.12467 | 218.7 | 0.16316 | 243 | 0.17745
[16 empty] | 194.4 | 0.041 |  |  | 198.9 | 0.047626 | 221 | 0.065023 | 206.1 | 0.069065 | 229 | 0.084373 | 210.6 | 0.10855 | 234 | 0.12467 | 219.6 | 0.16186 | 244 | 0.17675
[16 empty] | 195.3 | 0.041 |  |  | 199.8 | 0.047272 | 222 | 0.065023 | 207 | 0.068546 | 230 | 0.084373 | 211.5 | 0.10767 | 235 | 0.12467 | 220.5 | 0.16058 | 245 | 0.17606
[16 empty] | 196.2 | 0.041 |  |  | 200.7 | 0.046929 | 223 | 0.06231 | 207.9 | 0.068019 | 231 | 0.08301 | 212.4 | 0.10684 | 236 | 0.12328 | 221.4 | 0.1593 | 246 | 0.17467
[16 empty] | 197.1 | 0.041 |  |  | 201.6 | 0.046582 | 224 | 0.060901 | 208.8 | 0.067505 | 232 | 0.08301 | 213.3 | 0.10599 | 237 | 0.12328 | 222.3 | 0.15806 | 247 | 0.17467
[16 empty] | 198 | 0.04 |  |  | 202.5 | 0.046248 | 225 | 0.060901 | 209.7 | 0.066985 | 233 | 0.08301 | 214.2 | 0.10517 | 238 | 0.11911 | 223.2 | 0.15683 | 248 | 0.17328
[16 empty] | 198.9 | 0.04 |  |  | 203.4 | 0.045918 | 226 | 0.060901 | 210.6 | 0.066491 | 234 | 0.08301 | 215.1 | 0.10434 | 239 | 0.11911 | 224.1 | 0.1556 | 249 | 0.17328
[16 empty] | 199.8 | 0.04 |  |  | 204.3 | 0.045586 | 227 | 0.060901 | 211.5 | 0.065991 | 235 | 0.08301 | 216 | 0.10354 | 240 | 0.11841 | 225 | 0.15439 | 250 | 0.16911
[16 empty] | 200.7 | 0.04 |  |  | 205.2 | 0.045264 | 228 | 0.060183 | 212.4 | 0.065518 | 236 | 0.08301 | 216.9 | 0.10274 | 241 | 0.11772 | 225.9 | 0.15319 | 251 | 0.16842
[16 empty] | 201.6 | 0.04 |  |  | 206.1 | 0.044947 | 229 | 0.060182 | 213.3 | 0.065028 | 237 | 0.081649 | 217.8 | 0.10194 | 242 | 0.11772 | 226.8 | 0.152 | 252 | 0.16773
[16 empty] | 202.5 | 0.04 |  |  | 207 | 0.04463 | 230 | 0.060182 | 214.2 | 0.064557 | 238 | 0.081649 | 218.7 | 0.10117 | 243 | 0.11634 | 227.7 | 0.15085 | 253 | 0.16634
[16 empty] | 203.4 | 0.04 |  |  | 207.9 | 0.044313 | 231 | 0.059455 | 215.1 | 0.064081 | 239 | 0.081649 | 219.6 | 0.10041 | 244 | 0.11634 | 228.6 | 0.14971 | 254 | 0.16634
[16 empty] | 204.3 | 0.04 |  |  | 208.8 | 0.044018 | 232 | 0.059455 | 216 | 0.063619 | 240 | 0.077503 | 220.5 | 0.099644 | 245 | 0.11634 | 229.5 | 0.14857 | 255 | 0.16634
[16 empty] | 205.2 | 0.04 |  |  | 209.7 | 0.043708 | 233 | 0.059455 | 216.9 | 0.063161 | 241 | 0.077503 | 221.4 | 0.098884 | 246 | 0.11634 | 230.4 | 0.14745 | 256 | 0.16495
[16 empty] | 206.1 | 0.04 |  |  | 210.6 | 0.043415 | 234 | 0.059455 | 217.8 | 0.062704 | 242 | 0.077503 | 222.3 | 0.098154 | 247 | 0.11496 | 231.3 | 0.14634 | 257 | 0.16078
[16 empty] | 207 | 0.04 |  |  | 211.5 | 0.043117 | 235 | 0.059455 | 218.7 | 0.06226 | 243 | 0.076797 | 223.2 | 0.097424 | 248 | 0.11496 | 232.2 | 0.14524 | 258 | 0.16009
[16 empty] | 207.9 | 0.04 |  |  | 212.4 | 0.042844 | 236 | 0.057982 | 219.6 | 0.061821 | 244 | 0.076797 | 224.1 | 0.096697 | 249 | 0.11079 | 233.1 | 0.14416 | 259 | 0.15939
[16 empty] | 208.8 | 0.04 |  |  | 213.3 | 0.042545 | 500 | 0.051 | 220.5 | 0.061387 | 245 | 0.076797 | 225 | 0.09599 | 250 | 0.11079 | 234 | 0.14309 | 260 | 0.15939
[16 empty] | 209.7 | 0.04 |  |  | 214.2 | 0.042264 | 500 | 0.033 | 221.4 | 0.060948 | 246 | 0.076088 | 225.9 | 0.09528 | 251 | 0.1101 | 234.9 | 0.14204 | 261 | 0.158
[16 empty] | 210.6 | 0.04 |  |  | 215.1 | 0.042096 | 1000 | 0.033 | 222.3 | 0.060529 | 247 | 0.076088 | 226.8 | 0.094575 | 252 | 0.1101 | 235.8 | 0.14101 | 262 | 0.158
[16 empty] | 211.5 | 0.04 |  |  | 216 | 0.042044 | 6300 | 0.022 | 223.2 | 0.06011 | 248 | 0.076088 | 227.7 | 0.093904 | 253 | 0.1094 | 236.7 | 0.13997 | 263 | 0.15661
[16 empty] | 212.4 | 0.04 |  |  | 216.9 | 0.041979 |  |  | 224.1 | 0.059693 | 249 | 0.076088 | 228.6 | 0.093221 | 254 | 0.1094 | 237.6 | 0.13896 | 264 | 0.15661
[16 empty] | 213.3 | 0.04 |  |  | 217.8 | 0.041921 |  |  | 225 | 0.059286 | 250 | 0.07466 | 229.5 | 0.092549 | 255 | 0.108 | 238.5 | 0.13795 | 265 | 0.15245
[16 empty] | 214.2 | 0.04 |  |  | 218.7 | 0.041885 |  |  | 225.9 | 0.058876 | 251 | 0.07466 | 230.4 | 0.091881 | 256 | 0.108 | 239.4 | 0.13696 | 266 | 0.15175
[16 empty] | 215.1 | 0.04 |  |  | 219.6 | 0.041846 |  |  | 226.8 | 0.058471 | 252 | 0.074661 | 231.3 | 0.09124 | 257 | 0.108 | 240.3 | 0.13598 | 267 | 0.15106
[16 empty] | 216 | 0.04 |  |  | 220.5 | 0.041803 |  |  | 227.7 | 0.058082 | 253 | 0.074661 | 232.2 | 0.090578 | 258 | 0.108 | 241.2 | 0.13501 | 268 | 0.15106
[16 empty] | 216.9 | 0.04 |  |  | 221.4 | 0.041755 |  |  | 228.6 | 0.057698 | 254 | 0.074661 | 233.1 | 0.089933 | 259 | 0.1066 | 242.1 | 0.13404 | 269 | 0.14967
[16 empty] | 217.8 | 0.04 |  |  | 222.3 | 0.041729 |  |  | 229.5 | 0.057307 | 255 | 0.07466 | 234 | 0.089307 | 260 | 0.1066 | 243 | 0.13309 | 270 | 0.14967
[16 empty] | 218.7 | 0.04 |  |  | 223.2 | 0.041694 |  |  | 230.4 | 0.05692 | 256 | 0.07466 | 234.9 | 0.088683 | 261 | 0.10243 | 243.9 | 0.13216 | 271 | 0.14967
[16 empty] | 219.6 | 0.04 |  |  | 224.1 | 0.041649 |  |  | 231.3 | 0.056558 | 257 | 0.073231 | 235.8 | 0.088074 | 262 | 0.10243 | 244.8 | 0.13123 | 272 | 0.14828
[16 empty] | 220.5 | 0.04 |  |  | 225 | 0.041616 |  |  | 232.2 | 0.056168 | 258 | 0.073231 | 236.7 | 0.087456 | 263 | 0.10243 | 245.7 | 0.13031 | 273 | 0.14412
[16 empty] | 221.4 | 0.04 |  |  | 225.9 | 0.041572 |  |  | 233.1 | 0.055802 | 259 | 0.07323 | 237.6 | 0.086859 | 264 | 0.10174 | 246.6 | 0.12941 | 274 | 0.14412
[16 empty] | 222.3 | 0.04 |  |  | 226.8 | 0.041533 |  |  | 234 | 0.055445 | 260 | 0.069033 | 238.5 | 0.08627 | 265 | 0.10174 | 247.5 | 0.12851 | 275 | 0.14342
[16 empty] | 223.2 | 0.039 |  |  | 227.7 | 0.041512 |  |  | 234.9 | 0.055083 | 261 | 0.069033 | 239.4 | 0.085681 | 266 | 0.10105 | 248.4 | 0.12762 | 276 | 0.14273
[16 empty] | 224.1 | 0.039 |  |  | 228.6 | 0.041476 |  |  | 235.8 | 0.054735 | 262 | 0.069033 | 240.3 | 0.085096 | 267 | 0.10105 | 249.3 | 0.12674 | 277 | 0.14273
[16 empty] | 225 | 0.039 |  |  | 229.5 | 0.04144 |  |  | 236.7 | 0.054376 | 263 | 0.069033 | 241.2 | 0.084519 | 268 | 0.099673 | 250.2 | 0.12588 | 278 | 0.14134
[16 empty] | 225.9 | 0.039 |  |  | 230.4 | 0.041399 |  |  | 237.6 | 0.054039 | 264 | 0.068355 | 242.1 | 0.08395 | 269 | 0.099673 | 250.2 | 0.0072687 | 279 | 0.14134
[16 empty] | 226.8 | 0.039 |  |  | 231.3 | 0.041376 |  |  | 238.5 | 0.053692 | 265 | 0.068355 | 243 | 0.083384 | 270 | 0.099673 | 468 | 0.003 | 280 | 0.14134
[16 empty] | 227.7 | 0.039 |  |  | 232.2 | 0.041329 |  |  | 239.4 | 0.053362 | 266 | 0.068355 | 243.9 | 0.082834 | 271 | 0.099673 | 6300 | 0.003 | 281 | 0.13995
[16 empty] | 228.6 | 0.039 |  |  | 233.1 | 0.041292 |  |  | 240.3 | 0.053019 | 267 | 0.068355 | 244.8 | 0.082286 | 272 | 0.099673 |  |  | 282 | 0.13995
[16 empty] | 229.5 | 0.039 |  |  | 234 | 0.041262 |  |  | 241.2 | 0.052691 | 268 | 0.067683 | 245.7 | 0.081742 | 273 | 0.098297 |  |  | 283 | 0.13578
[16 empty] | 230.4 | 0.039 |  |  | 234.9 | 0.04123 |  |  | 242.1 | 0.052361 | 269 | 0.067683 | 246.6 | 0.081203 | 274 | 0.098297 |  |  | 284 | 0.13578
[16 empty] | 231.3 | 0.039 |  |  | 235.8 | 0.041208 |  |  | 243 | 0.052037 | 270 | 0.067683 | 247.5 | 0.080675 | 275 | 0.098297 |  |  | 285 | 0.13508
[16 empty] | 232.2 | 0.039 |  |  | 236.7 | 0.041169 |  |  | 243.9 | 0.051717 | 271 | 0.067683 | 248.4 | 0.080142 | 276 | 0.09414 |  |  | 286 | 0.13439
[16 empty] | 233.1 | 0.039 |  |  | 237.6 | 0.041139 |  |  | 244.8 | 0.051409 | 272 | 0.067683 | 249.3 | 0.07962 | 277 | 0.09414 |  |  | 287 | 0.13439
[16 empty] | 234 | 0.039 |  |  | 238.5 | 0.041106 |  |  | 245.7 | 0.051087 | 273 | 0.066351 | 250.2 | 0.079114 | 278 | 0.09414 |  |  | 288 | 0.133
[16 empty] | 234.9 | 0.039 |  |  | 239.4 | 0.041077 |  |  | 246.6 | 0.050786 | 274 | 0.066351 | 250.2 | 0.0072687 | 279 | 0.09344 |  |  | 289 | 0.133
[16 empty] | 235.8 | 0.039 |  |  | 240.3 | 0.041042 |  |  | 247.5 | 0.050478 | 275 | 0.066351 | 288 | 0.0067981 | 280 | 0.09344 |  |  | 290 | 0.133
[16 empty] | 236.7 | 0.039 |  |  | 241.2 | 0.041015 |  |  | 248.4 | 0.050175 | 276 | 0.066351 | 297 | 0.0064401 | 281 | 0.092739 |  |  | 291 | 0.133
[16 empty] | 237.6 | 0.039 |  |  | 242.1 | 0.040974 |  |  | 249.3 | 0.049874 | 277 | 0.066351 | 306 | 0.0061667 | 282 | 0.092739 |  |  | 292 | 0.13162
[16 empty] | 238.5 | 0.039 |  |  | 243 | 0.040948 |  |  | 250.2 | 0.049578 | 278 | 0.066351 | 315 | 0.0058962 | 283 | 0.092739 |  |  | 293 | 0.13162
[16 empty] | 239.4 | 0.039 |  |  | 243.9 | 0.040913 |  |  | 250.2 | 0.0072687 | 279 | 0.066351 | 324 | 0.0056779 | 284 | 0.091332 |  |  | 294 | 0.12745
[16 empty] | 240.3 | 0.039 |  |  | 244.8 | 0.040888 |  |  | 468 | 0.003 | 280 | 0.066351 | 333 | 0.0054841 | 285 | 0.091332 |  |  | 295 | 0.12745
[16 empty] | 241.2 | 0.039 |  |  | 245.7 | 0.040853 |  |  | 6300 | 0.003 | 281 | 0.066351 | 342 | 0.0053097 | 286 | 0.091333 |  |  | 296 | 0.12676
[16 empty] | 242.1 | 0.039 |  |  | 246.6 | 0.040827 |  |  |  |  | 282 | 0.065023 | 351 | 0.0051517 | 287 | 0.091333 |  |  | 297 | 0.12606
[16 empty] | 243 | 0.039 |  |  | 247.5 | 0.040798 |  |  |  |  | 283 | 0.065023 | 360 | 0.0050073 | 288 | 0.091333 |  |  | 298 | 0.12606
[16 empty] | 243.9 | 0.039 |  |  | 248.4 | 0.040767 |  |  |  |  | 284 | 0.065023 | 369 | 0.0048746 | 289 | 0.091332 |  |  | 300 | 0.12606
[16 empty] | 244.8 | 0.039 |  |  | 249.3 | 0.040738 |  |  |  |  | 285 | 0.065023 | 378 | 0.0047517 | 290 | 0.089925 |  |  | 300 | 0.060901
[16 empty] | 245.7 | 0.039 |  |  | 250.2 | 0.040712 |  |  |  |  | 286 | 0.065023 | 387 | 0.0046377 | 291 | 0.089925 |  |  | 500 | 0.052
[16 empty] | 246.6 | 0.039 |  |  | 250.2 | 0.0072687 |  |  |  |  | 287 | 0.064354 | 396 | 0.0040105 | 292 | 0.089925 |  |  | 500 | 0.033
[16 empty] | 247.5 | 0.039 |  |  | 288 | 0.0067981 |  |  |  |  | 288 | 0.060901 | 405 | 0.003911 | 293 | 0.085744 |  |  | 1000 | 0.033
[16 empty] | 248.4 | 0.039 |  |  | 297 | 0.0064401 |  |  |  |  | 289 | 0.060901 | 414 | 0.0038178 | 294 | 0.085744 |  |  | 6300 | 0.022
[16 empty] | 249.3 | 0.038 |  |  | 306 | 0.0061667 |  |  |  |  | 290 | 0.060901 | 423 | 0.0037299 | 295 | 0.085744
[16 empty] | 250.2 | 0.038 |  |  | 315 | 0.0058962 |  |  |  |  | 291 | 0.060901 | 432 | 0.0036472 | 296 | 0.085057
[16 empty] | 250.2 | 0.007 |  |  | 324 | 0.0056779 |  |  |  |  | 292 | 0.060901 | 441 | 0.003569 | 297 | 0.085057
[16 empty] | 468 | 0.003 |  |  | 333 | 0.0054841 |  |  |  |  | 293 | 0.060182 | 450 | 0.0034949 | 298 | 0.084373
[16 empty] | 6300 | 0.003 |  |  | 342 | 0.0053097 |  |  |  |  | 294 | 0.060183 | 459 | 0.0034246 | 299 | 0.084373
[20 empty] | 351 | 0.0051517 |  |  |  |  | 295 | 0.060182 | 468 | 0.003 | 300 | 0.060183
[20 empty] | 360 | 0.0050073 |  |  |  |  | 296 | 0.060182 | 6300 | 0.003 | 500 | 0.052
[20 empty] | 369 | 0.0048746 |  |  |  |  | 297 | 0.060182 |  |  | 500 | 0.033
[20 empty] | 378 | 0.0047517 |  |  |  |  | 298 | 0.059455 |  |  | 1000 | 0.033
[20 empty] | 387 | 0.0046377 |  |  |  |  | 299 | 0.059455 |  |  | 6300 | 0.022
[20 empty] | 396 | 0.0040105 |  |  |  |  | 300 | 0.057982
[20 empty] | 405 | 0.003911 |  |  |  |  | 500 | 0.052
[20 empty] | 414 | 0.0038178 |  |  |  |  | 500 | 0.033
[20 empty] | 423 | 0.0037299 |  |  |  |  | 1000 | 0.033
[20 empty] | 432 | 0.0036472 |  |  |  |  | 6300 | 0.022
[20 empty] | 441 | 0.003569
[20 empty] | 450 | 0.0034949
[20 empty] | 459 | 0.0034246
[20 empty] | 468 | 0.003
[20 empty] | 6300 | 0.003

## S&C "KS" Speed
S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter
S&C "KS" Speed | [11 empty] | S&C "KS" Speed | [11 empty] | S&C "KS" Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025
Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information.
2KS |  |  |  | 3KS |  |  |  | 5KS |  |  |  | 7KS |  |  |  | 10KS |  |  |  | 15KS |  |  |  | 20KS
Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s
3 | 301.34 | 4 | 301.356 | 5 | 301.34 | 6 | 301.356 | 9 | 302.48 | 10 | 302.494 | 12.6 | 256.439 | 14 | 256.456 | 18 | 248.08 | 20 | 248.094 | 27 | 301.34 | 30 | 301.356 | 36 | 301.502 | 40 | 301.518
4 | 77.118 | 5 | 77.133 | 6 | 100.924 | 7 | 100.941 | 9.9 | 161.258 | 11 | 161.275 | 13.5 | 161.281 | 15 | 161.296 | 18.9 | 155.239 | 21 | 155.254 | 27.9 | 210.859 | 31 | 210.875 | 36.9 | 202.942 | 41 | 202.958
5 | 46.882 | 6 | 46.896 | 7 | 47.419 | 8 | 47.433 | 10.8 | 102.103 | 12 | 102.116 | 14.4 | 95.94 | 16 | 95.954 | 19.8 | 119.968 | 22 | 119.983 | 28.8 | 134.15 | 32 | 134.166 | 37.8 | 151.109 | 42 | 151.125
6 | 31.74 | 7 | 31.754 | 8 | 35.529 | 9 | 35.543 | 11.7 | 63.566 | 13 | 63.583 | 15.3 | 74.683 | 17 | 74.7 | 20.7 | 91.575 | 23 | 91.591 | 29.7 | 120.55 | 33 | 120.566 | 38.7 | 119.571 | 43 | 119.585
7 | 26.183 | 8 | 26.2 | 9 | 27.517 | 10 | 27.533 | 12.6 | 48.333 | 14 | 48.35 | 16.2 | 60.856 | 18 | 60.871 | 21.6 | 79.88 | 24 | 79.893 | 30.6 | 106.953 | 34 | 106.968 | 39.6 | 100.888 | 44 | 100.902
8 | 17.01 | 9 | 17.025 | 9.9 | 21.69 | 11 | 21.704 | 13.5 | 38.366 | 15 | 38.383 | 17.1 | 47.028 | 19 | 47.041 | 22.5 | 68.185 | 25 | 68.2 | 31.5 | 82.313 | 35 | 82.327 | 40.5 | 80.081 | 45 | 80.096
9 | 13.409 | 10 | 13.425 | 10.8 | 17.347 | 12 | 17.362 | 14.4 | 28.913 | 16 | 28.927 | 18 | 36.16 | 20 | 36.175 | 23.4 | 53.577 | 26 | 53.591 | 32.4 | 65.42 | 36 | 65.435 | 41.4 | 73.705 | 46 | 73.718
9.9 | 9.034 | 11 | 9.05 | 11.7 | 15.539 | 13 | 15.552 | 15.3 | 26.047 | 17 | 26.06 | 18.9 | 31.881 | 21 | 31.896 | 24.3 | 46.819 | 27 | 46.833 | 33.3 | 59.498 | 37 | 59.512 | 42.3 | 67.329 | 47 | 67.343
10.8 | 6.87 | 12 | 6.885 | 12.6 | 13.731 | 14 | 13.746 | 16.2 | 23.181 | 18 | 23.196 | 19.8 | 27.603 | 22 | 27.616 | 25.2 | 40.06 | 28 | 40.075 | 34.2 | 53.577 | 38 | 53.591 | 43.2 | 60.949 | 48 | 60.966
11.7 | 4.993 | 13 | 5.008 | 13.5 | 12.379 | 15 | 12.393 | 17.1 | 18.513 | 19 | 18.527 | 20.7 | 21.468 | 23 | 21.483 | 26.1 | 35.542 | 29 | 35.558 | 35.1 | 44.796 | 39 | 44.81 | 44.1 | 50.81 | 49 | 50.825
12.6 | 3.829 | 14 | 3.843 | 14.4 | 11.027 | 16 | 11.041 | 18 | 16.547 | 20 | 16.56 | 21.6 | 19.668 | 24 | 19.683 | 27 | 31.026 | 30 | 31.041 | 36 | 41.457 | 40 | 41.475 | 45 | 47.185 | 50 | 47.2
13.5 | 3.011 | 15 | 3.027 | 15.3 | 9.901 | 17 | 9.916 | 18.9 | 14.58 | 21 | 14.593 | 22.5 | 17.869 | 25 | 17.883 | 27.9 | 28.505 | 31 | 28.518 | 36.9 | 38.119 | 41 | 38.133 | 45.9 | 43.557 | 51 | 43.575
14.4 | 2.332 | 16 | 2.35 | 16.2 | 8.775 | 18 | 8.791 | 19.8 | 13.235 | 22 | 13.25 | 23.4 | 16.069 | 26 | 16.083 | 28.8 | 25.985 | 32 | 26 | 37.8 | 31.971 | 42 | 31.985 | 46.8 | 39.931 | 52 | 39.946
15.3 | 2.005 | 17 | 2.018 | 17.1 | 8.175 | 19 | 8.191 | 20.7 | 11.891 | 23 | 11.908 | 24.3 | 14.629 | 27 | 14.643 | 29.7 | 23.464 | 33 | 23.479 | 38.7 | 30.114 | 43 | 30.129 | 47.7 | 37.922 | 53 | 37.935
16.2 | 1.678 | 18 | 1.691 | 18 | 7.575 | 20 | 7.591 | 21.6 | 9.865 | 24 | 9.879 | 25.2 | 13.189 | 28 | 13.202 | 30.6 | 22.067 | 34 | 22.083 | 39.6 | 28.258 | 44 | 28.275 | 48.6 | 35.911 | 54 | 35.927
17.1 | 1.518 | 19 | 1.533 | 18.9 | 6.975 | 21 | 6.991 | 22.5 | 9.264 | 25 | 9.277 | 26.1 | 12.269 | 29 | 12.283 | 31.5 | 20.67 | 35 | 20.685 | 40.5 | 26.401 | 45 | 26.416 | 49.5 | 33.901 | 55 | 33.916
18 | 1.358 | 20 | 1.375 | 19.8 | 4.8 | 22 | 4.816 | 23.4 | 8.663 | 26 | 8.677 | 27 | 11.349 | 30 | 11.366 | 32.4 | 19.272 | 36 | 19.287 | 41.4 | 24.342 | 46 | 24.358 | 50.4 | 31.891 | 56 | 31.908
18.9 | 1.198 | 21 | 1.212 | 20.7 | 4.231 | 23 | 4.246 | 24.3 | 6.825 | 27 | 6.841 | 27.9 | 10.429 | 31 | 10.443 | 33.3 | 17.875 | 37 | 17.891 | 42.3 | 22.282 | 47 | 22.296 | 51.3 | 29.882 | 57 | 29.9
19.8 | 1.084 | 22 | 1.1 | 21.6 | 3.663 | 24 | 3.677 | 25.2 | 5.697 | 28 | 5.71 | 28.8 | 9.892 | 32 | 9.908 | 34.2 | 16.836 | 38 | 16.85 | 43.2 | 21.112 | 48 | 21.127 | 52.2 | 27.384 | 58 | 27.4
20.7 | 0.97 | 23 | 0.985 | 22.5 | 3.279 | 25 | 3.293 | 26.1 | 5.061 | 29 | 5.077 | 29.7 | 9.355 | 33 | 9.368 | 35.1 | 15.796 | 39 | 15.81 | 44.1 | 19.941 | 49 | 19.958 | 53.1 | 24.887 | 59 | 24.902
21.6 | 0.857 | 24 | 0.871 | 23.4 | 2.895 | 26 | 2.91 | 27 | 4.426 | 30 | 4.441 | 30.6 | 8.818 | 34 | 8.833 | 36 | 14.757 | 40 | 14.771 | 45 | 18.771 | 50 | 18.785 | 54 | 23.896 | 60 | 23.91
22.5 | 0.797 | 25 | 0.81 | 24.3 | 2.62 | 27 | 2.635 | 27.9 | 3.725 | 31 | 3.741 | 31.5 | 8.282 | 35 | 8.296 | 36.9 | 13.717 | 41 | 13.733 | 45.9 | 17.601 | 51 | 17.616 | 54.9 | 22.906 | 61 | 22.918
23.4 | 0.737 | 26 | 0.752 | 25.2 | 2.346 | 28 | 2.36 | 28.8 | 3.479 | 32 | 3.493 | 32.4 | 7.855 | 36 | 7.868 | 37.8 | 13.057 | 42 | 13.071 | 46.8 | 16.584 | 52 | 16.6 | 55.8 | 21.915 | 62 | 21.929
24.3 | 0.677 | 27 | 0.691 | 26.1 | 2.196 | 29 | 2.21 | 29.7 | 3.233 | 33 | 3.25 | 33.3 | 7.429 | 37 | 7.443 | 38.7 | 12.398 | 43 | 12.412 | 47.7 | 15.567 | 53 | 15.583 | 56.7 | 20.925 | 63 | 20.941
25.2 | 0.617 | 28 | 0.633 | 27 | 2.045 | 30 | 2.06 | 30.6 | 3.064 | 34 | 3.079 | 34.2 | 7.003 | 38 | 7.016 | 39.6 | 11.738 | 44 | 11.752 | 48.6 | 14.551 | 54 | 14.566 | 57.6 | 19.934 | 64 | 19.95
26.1 | 0.58 | 29 | 0.593 | 27.9 | 1.896 | 31 | 1.91 | 31.5 | 2.897 | 35 | 2.91 | 35.1 | 6.577 | 39 | 6.591 | 40.5 | 11.078 | 45 | 11.093 | 49.5 | 13.781 | 55 | 13.793 | 58.5 | 19.096 | 65 | 19.11
27 | 0.542 | 30 | 0.558 | 28.8 | 1.746 | 32 | 1.76 | 32.4 | 2.729 | 36 | 2.743 | 36 | 6.271 | 40 | 6.285 | 41.4 | 10.418 | 46 | 10.433 | 50.4 | 13.011 | 56 | 13.025 | 59.4 | 18.257 | 66 | 18.275
27.9 | 0.504 | 31 | 0.518 | 29.7 | 1.637 | 33 | 1.652 | 33.3 | 2.558 | 37 | 2.575 | 36.9 | 5.966 | 41 | 5.979 | 42.3 | 10.017 | 47 | 10.033 | 51.3 | 12.241 | 57 | 12.254 | 60.3 | 17.419 | 67 | 17.433
28.8 | 0.466 | 32 | 0.483 | 30.6 | 1.529 | 34 | 1.543 | 34.2 | 2.388 | 38 | 2.402 | 37.8 | 5.66 | 42 | 5.675 | 43.2 | 9.615 | 48 | 9.629 | 52.2 | 11.471 | 58 | 11.485 | 61.2 | 16.581 | 68 | 16.596
29.7 | 0.447 | 33 | 0.46 | 31.5 | 1.421 | 35 | 1.435 | 35.1 | 2.218 | 39 | 2.233 | 38.7 | 5.354 | 43 | 5.368 | 44.1 | 9.214 | 49 | 9.227 | 53.1 | 11.099 | 59 | 11.112 | 62.1 | 15.742 | 69 | 15.758
30.6 | 0.428 | 34 | 0.441 | 32.4 | 1.313 | 36 | 1.327 | 36 | 2.134 | 40 | 2.15 | 39.6 | 5.079 | 44 | 5.093 | 45 | 8.812 | 50 | 8.827 | 54 | 10.727 | 60 | 10.741 | 63 | 14.904 | 70 | 14.918
31.5 | 0.409 | 35 | 0.425 | 33.3 | 1.25 | 37 | 1.266 | 36.9 | 2.051 | 41 | 2.066 | 40.5 | 4.804 | 45 | 4.818 | 45.9 | 8.411 | 51 | 8.425 | 54.9 | 10.355 | 61 | 10.368 | 63.9 | 14.328 | 71 | 14.341
32.4 | 0.39 | 36 | 0.404 | 34.2 | 1.187 | 38 | 1.202 | 37.8 | 1.967 | 42 | 1.983 | 41.4 | 4.529 | 46 | 4.543 | 46.8 | 8.072 | 52 | 8.085 | 55.8 | 9.983 | 62 | 10 | 64.8 | 13.752 | 72 | 13.766
33.3 | 0.371 | 37 | 0.385 | 35.1 | 1.124 | 39 | 1.141 | 38.7 | 1.883 | 43 | 1.9 | 42.3 | 4.287 | 47 | 4.302 | 47.7 | 7.732 | 53 | 7.746 | 56.7 | 9.612 | 63 | 9.627 | 65.7 | 13.175 | 73 | 13.191
34.2 | 0.354 | 38 | 0.368 | 36 | 1.061 | 40 | 1.075 | 39.6 | 1.716 | 44 | 1.733 | 43.2 | 4.043 | 48 | 4.058 | 48.6 | 7.393 | 54 | 7.408 | 57.6 | 9.259 | 64 | 9.275 | 66.6 | 12.599 | 74 | 12.612
35.1 | 0.338 | 39 | 0.352 | 36.9 | 0.998 | 41 | 1.012 | 40.5 | 1.636 | 45 | 1.65 | 44.1 | 3.8 | 49 | 3.816 | 49.5 | 7.054 | 55 | 7.068 | 58.5 | 8.906 | 65 | 8.921 | 67.5 | 12.023 | 75 | 12.037
36 | 0.321 | 40 | 0.335 | 37.8 | 0.957 | 42 | 0.971 | 41.4 | 1.556 | 46 | 1.568 | 45 | 3.634 | 50 | 3.65 | 50.4 | 6.714 | 56 | 6.729 | 59.4 | 8.554 | 66 | 8.568 | 68.4 | 11.633 | 76 | 11.65
36.9 | 0.305 | 41 | 0.318 | 38.7 | 0.915 | 43 | 0.929 | 42.3 | 1.475 | 47 | 1.491 | 45.9 | 3.469 | 51 | 3.483 | 51.3 | 6.513 | 57 | 6.527 | 60.3 | 8.201 | 67 | 8.216 | 69.3 | 11.243 | 77 | 11.258
37.8 | 0.288 | 42 | 0.302 | 39.6 | 0.873 | 44 | 0.887 | 43.2 | 1.395 | 48 | 1.41 | 46.8 | 3.303 | 52 | 3.316 | 52.2 | 6.311 | 58 | 6.327 | 61.2 | 7.849 | 68 | 7.862 | 70.2 | 10.854 | 78 | 10.868
38.7 | 0.277 | 43 | 0.291 | 40.5 | 0.831 | 45 | 0.846 | 44.1 | 1.315 | 49 | 1.329 | 47.7 | 3.137 | 53 | 3.152 | 53.1 | 6.11 | 59 | 6.125 | 62.1 | 7.624 | 69 | 7.641 | 71.1 | 10.464 | 79 | 10.477
39.6 | 0.266 | 44 | 0.283 | 41.4 | 0.789 | 46 | 0.804 | 45 | 1.268 | 50 | 1.283 | 48.6 | 2.995 | 54 | 3.01 | 54 | 5.909 | 60 | 5.925 | 63 | 7.4 | 70 | 7.416 | 72 | 10.074 | 80 | 10.087
40.5 | 0.255 | 45 | 0.268 | 42.3 | 0.747 | 47 | 0.76 | 45.9 | 1.22 | 51 | 1.235 | 49.5 | 2.854 | 55 | 2.868 | 54.9 | 5.707 | 61 | 5.725 | 63.9 | 7.176 | 71 | 7.191 | 72.9 | 9.79 | 81 | 9.804
41.4 | 0.244 | 46 | 0.258 | 43.2 | 0.722 | 48 | 0.735 | 46.8 | 1.173 | 52 | 1.187 | 50.4 | 2.712 | 56 | 2.727 | 55.8 | 5.506 | 62 | 5.521 | 64.8 | 6.951 | 72 | 6.966 | 73.8 | 9.505 | 82 | 9.518
42.3 | 0.233 | 47 | 0.25 | 44.1 | 0.697 | 49 | 0.71 | 47.7 | 1.125 | 53 | 1.141 | 51.3 | 2.571 | 57 | 2.585 | 56.7 | 5.305 | 63 | 5.318 | 65.7 | 6.727 | 73 | 6.741 | 74.7 | 9.221 | 83 | 9.235
43.2 | 0.222 | 48 | 0.235 | 45 | 0.672 | 50 | 0.685 | 48.6 | 1.078 | 54 | 1.091 | 52.2 | 2.476 | 58 | 2.491 | 57.6 | 5.148 | 64 | 5.162 | 66.6 | 6.503 | 74 | 6.516 | 75.6 | 8.936 | 84 | 8.95
44.1 | 0.215 | 49 | 0.229 | 45.9 | 0.646 | 51 | 0.66 | 49.5 | 1.031 | 55 | 1.043 | 53.1 | 2.381 | 59 | 2.396 | 58.5 | 4.991 | 65 | 5.008 | 67.5 | 6.335 | 75 | 6.35 | 76.5 | 8.605 | 85 | 8.618
45 | 0.208 | 50 | 0.225 | 46.8 | 0.621 | 52 | 0.635 | 50.4 | 0.983 | 56 | 1 | 54 | 2.286 | 60 | 2.3 | 59.4 | 4.834 | 66 | 4.85 | 68.4 | 6.167 | 76 | 6.183 | 77.4 | 8.274 | 86 | 8.287
45.9 | 0.201 | 51 | 0.216 | 47.7 | 0.596 | 53 | 0.61 | 51.3 | 0.936 | 57 | 0.95 | 54.9 | 2.191 | 61 | 2.208 | 60.3 | 4.678 | 67 | 4.691 | 69.3 | 5.999 | 77 | 6.012 | 78.3 | 7.943 | 87 | 7.958
46.8 | 0.194 | 52 | 0.208 | 48.6 | 0.571 | 54 | 0.585 | 52.2 | 0.91 | 58 | 0.925 | 55.8 | 2.096 | 62 | 2.11 | 61.2 | 4.521 | 68 | 4.535 | 70.2 | 5.831 | 78 | 5.846 | 79.2 | 7.747 | 88 | 7.76
47.7 | 0.187 | 53 | 0.202 | 49.5 | 0.551 | 55 | 0.566 | 53.1 | 0.883 | 59 | 0.9 | 56.7 | 2.031 | 63 | 2.046 | 62.1 | 4.364 | 69 | 4.377 | 71.1 | 5.663 | 79 | 5.677 | 80.1 | 7.55 | 89 | 7.566
48.6 | 0.18 | 54 | 0.194 | 50.4 | 0.53 | 56 | 0.543 | 54 | 0.857 | 60 | 0.871 | 57.6 | 1.966 | 64 | 1.983 | 63 | 4.258 | 70 | 4.275 | 72 | 5.495 | 80 | 5.51 | 81 | 7.354 | 90 | 7.368
49.5 | 0.173 | 55 | 0.19 | 51.3 | 0.51 | 57 | 0.525 | 54.9 | 0.83 | 61 | 0.843 | 58.5 | 1.901 | 65 | 1.916 | 63.9 | 4.152 | 71 | 4.166 | 72.9 | 5.327 | 81 | 5.341 | 81.9 | 7.158 | 91 | 7.175
50.4 | 0.167 | 56 | 0.183 | 52.2 | 0.49 | 58 | 0.504 | 55.8 | 0.804 | 62 | 0.818 | 59.4 | 1.836 | 66 | 1.85 | 64.8 | 4.046 | 72 | 4.06 | 73.8 | 5.216 | 82 | 5.233 | 82.8 | 6.962 | 92 | 6.977
51.3 | 0.16 | 57 | 0.176 | 53.1 | 0.47 | 59 | 0.485 | 56.7 | 0.778 | 63 | 0.791 | 60.3 | 1.771 | 67 | 1.785 | 65.7 | 3.94 | 73 | 3.954 | 74.7 | 5.106 | 83 | 5.118 | 83.7 | 6.821 | 93 | 6.835
52.2 | 0.156 | 58 | 0.173 | 54 | 0.45 | 60 | 0.466 | 57.6 | 0.751 | 64 | 0.766 | 61.2 | 1.706 | 68 | 1.718 | 66.6 | 3.834 | 74 | 3.85 | 75.6 | 4.995 | 84 | 5.01 | 84.6 | 6.68 | 94 | 6.693
53.1 | 0.152 | 59 | 0.168 | 54.9 | 0.439 | 61 | 0.452 | 58.5 | 0.725 | 65 | 0.741 | 62.1 | 1.641 | 69 | 1.658 | 67.5 | 3.729 | 75 | 3.743 | 76.5 | 4.884 | 85 | 4.9 | 85.5 | 6.539 | 95 | 6.552
54 | 0.148 | 60 | 0.165 | 55.8 | 0.428 | 62 | 0.441 | 59.4 | 0.699 | 66 | 0.712 | 63 | 1.601 | 70 | 1.616 | 68.4 | 3.623 | 76 | 3.637 | 77.4 | 4.774 | 86 | 4.787 | 86.4 | 6.398 | 96 | 6.412
54.9 | 0.144 | 61 | 0.16 | 56.7 | 0.416 | 63 | 0.433 | 60.3 | 0.672 | 67 | 0.685 | 63.9 | 1.561 | 71 | 1.575 | 69.3 | 3.517 | 77 | 3.533 | 78.3 | 4.663 | 87 | 4.677 | 87.3 | 6.257 | 97 | 6.271
55.8 | 0.141 | 62 | 0.158 | 57.6 | 0.405 | 64 | 0.418 | 61.2 | 0.658 | 68 | 0.675 | 64.8 | 1.522 | 72 | 1.535 | 70.2 | 3.443 | 78 | 3.458 | 79.2 | 4.552 | 88 | 4.566 | 88.2 | 6.116 | 98 | 6.133
56.7 | 0.137 | 63 | 0.152 | 58.5 | 0.394 | 65 | 0.408 | 62.1 | 0.643 | 69 | 0.658 | 65.7 | 1.482 | 73 | 1.5 | 71.1 | 3.368 | 79 | 3.383 | 80.1 | 4.441 | 89 | 4.458 | 89.1 | 5.975 | 99 | 5.991
57.6 | 0.133 | 64 | 0.15 | 59.4 | 0.383 | 66 | 0.4 | 63 | 0.629 | 70 | 0.643 | 66.6 | 1.442 | 74 | 1.458 | 72 | 3.294 | 80 | 3.308 | 81 | 4.349 | 90 | 4.362 | 90 | 5.852 | 100 | 5.866
58.5 | 0.129 | 65 | 0.144 | 60.3 | 0.372 | 67 | 0.385 | 63.9 | 0.614 | 71 | 0.629 | 67.5 | 1.403 | 75 | 1.416 | 72.9 | 3.22 | 81 | 3.235 | 81.9 | 4.256 | 91 | 4.268 | 90.9 | 5.73 | 101 | 5.743
59.4 | 0.125 | 66 | 0.141 | 61.2 | 0.361 | 68 | 0.375 | 64.8 | 0.6 | 72 | 0.616 | 68.4 | 1.363 | 76 | 1.377 | 73.8 | 3.146 | 82 | 3.16 | 82.8 | 4.163 | 92 | 4.177 | 91.8 | 5.607 | 102 | 5.621
60.3 | 0.122 | 67 | 0.136 | 62.1 | 0.35 | 69 | 0.366 | 65.7 | 0.585 | 73 | 0.6 | 69.3 | 1.324 | 77 | 1.337 | 74.7 | 3.072 | 83 | 3.085 | 83.7 | 4.07 | 93 | 4.085 | 92.7 | 5.484 | 103 | 5.5
61.2 | 0.118 | 68 | 0.133 | 63 | 0.339 | 70 | 0.354 | 66.6 | 0.571 | 74 | 0.585 | 70.2 | 1.284 | 78 | 1.3 | 75.6 | 2.998 | 84 | 3.012 | 84.6 | 3.977 | 94 | 3.991 | 93.6 | 5.361 | 104 | 5.375
62.1 | 0.115 | 69 | 0.133 | 63.9 | 0.328 | 71 | 0.343 | 67.5 | 0.556 | 75 | 0.571 | 71.1 | 1.244 | 79 | 1.258 | 76.5 | 2.923 | 85 | 2.937 | 85.5 | 3.884 | 95 | 3.9 | 94.5 | 5.238 | 105 | 5.252
63 | 0.113 | 70 | 0.127 | 64.8 | 0.321 | 72 | 0.335 | 68.4 | 0.542 | 76 | 0.558 | 72 | 1.205 | 80 | 1.218 | 77.4 | 2.849 | 86 | 2.866 | 86.4 | 3.791 | 96 | 3.808 | 95.4 | 5.115 | 106 | 5.129
63.9 | 0.111 | 71 | 0.126 | 65.7 | 0.313 | 73 | 0.327 | 69.3 | 0.527 | 77 | 0.541 | 72.9 | 1.165 | 81 | 1.179 | 78.3 | 2.799 | 87 | 2.816 | 87.3 | 3.698 | 97 | 3.712 | 96.3 | 4.993 | 107 | 5.008
64.8 | 0.108 | 72 | 0.125 | 66.6 | 0.306 | 74 | 0.321 | 70.2 | 0.513 | 78 | 0.527 | 73.8 | 1.14 | 82 | 1.154 | 79.2 | 2.748 | 88 | 2.762 | 88.2 | 3.605 | 98 | 3.618 | 97.2 | 4.89 | 108 | 4.904
65.7 | 0.106 | 73 | 0.123 | 67.5 | 0.299 | 75 | 0.312 | 71.1 | 0.498 | 79 | 0.512 | 74.7 | 1.115 | 83 | 1.129 | 80.1 | 2.698 | 89 | 2.712 | 89.1 | 3.546 | 99 | 3.56 | 98.1 | 4.787 | 109 | 4.802
66.6 | 0.103 | 74 | 0.118 | 68.4 | 0.291 | 76 | 0.308 | 72 | 0.484 | 80 | 0.5 | 75.6 | 1.09 | 84 | 1.104 | 81 | 2.648 | 90 | 2.662 | 90 | 3.487 | 100 | 3.502 | 99 | 4.684 | 110 | 4.7
67.5 | 0.101 | 75 | 0.116 | 69.3 | 0.284 | 77 | 0.3 | 72.9 | 0.469 | 81 | 0.483 | 76.5 | 1.066 | 85 | 1.083 | 81.9 | 2.597 | 91 | 2.61 | 90.9 | 3.427 | 101 | 3.441 | 99.9 | 4.581 | 111 | 4.596
68.4 | 0.098 | 76 | 0.115 | 70.2 | 0.277 | 78 | 0.291 | 73.8 | 0.455 | 82 | 0.468 | 77.4 | 1.041 | 86 | 1.058 | 82.8 | 2.547 | 92 | 2.56 | 91.8 | 3.368 | 102 | 3.383 | 100.8 | 4.478 | 112 | 4.491
69.3 | 0.096 | 77 | 0.111 | 71.1 | 0.269 | 79 | 0.283 | 74.7 | 0.441 | 83 | 0.458 | 78.3 | 1.016 | 87 | 1.033 | 83.7 | 2.497 | 93 | 2.51 | 92.7 | 3.309 | 103 | 3.325 | 101.7 | 4.388 | 113 | 4.402
70.2 | 0.094 | 78 | 0.109 | 72 | 0.262 | 80 | 0.277 | 75.6 | 0.426 | 84 | 0.441 | 79.2 | 0.991 | 88 | 1.008 | 84.6 | 2.446 | 94 | 2.46 | 93.6 | 3.249 | 104 | 3.266 | 102.6 | 4.298 | 114 | 4.312
71.1 | 0.091 | 79 | 0.108 | 72.9 | 0.256 | 81 | 0.271 | 76.5 | 0.419 | 85 | 0.433 | 80.1 | 0.966 | 89 | 0.983 | 85.5 | 2.396 | 95 | 2.41 | 94.5 | 3.19 | 105 | 3.204 | 103.5 | 4.208 | 115 | 4.225
72 | 0.089 | 80 | 0.107 | 73.8 | 0.251 | 82 | 0.266 | 77.4 | 0.411 | 86 | 0.425 | 81 | 0.941 | 90 | 0.958 | 86.4 | 2.332 | 96 | 2.35 | 95.4 | 3.131 | 106 | 3.146 | 104.4 | 4.119 | 116 | 4.133
72.9 | 0.087 | 81 | 0.102 | 74.7 | 0.245 | 83 | 0.26 | 78.3 | 0.404 | 87 | 0.418 | 81.9 | 0.916 | 91 | 0.933 | 87.3 | 2.269 | 97 | 2.283 | 96.3 | 3.072 | 107 | 3.085 | 105.3 | 4.029 | 117 | 4.043
73.8 | 0.085 | 82 | 0.101 | 75.6 | 0.239 | 84 | 0.254 | 79.2 | 0.396 | 88 | 0.41 | 82.8 | 0.891 | 92 | 0.908 | 88.2 | 2.205 | 98 | 2.218 | 97.2 | 3.012 | 108 | 3.027 | 106.2 | 3.96 | 118 | 3.975
74.7 | 0.083 | 83 | 0.1 | 76.5 | 0.234 | 85 | 0.25 | 80.1 | 0.389 | 89 | 0.404 | 83.7 | 0.867 | 93 | 0.883 | 89.1 | 2.142 | 99 | 2.158 | 98.1 | 2.953 | 109 | 2.966 | 107.1 | 3.892 | 119 | 3.908
75.6 | 0.082 | 84 | 0.1 | 77.4 | 0.228 | 86 | 0.243 | 81 | 0.382 | 90 | 0.396 | 84.6 | 0.851 | 94 | 0.866 | 90 | 2.079 | 100 | 2.093 | 99 | 2.894 | 110 | 2.908 | 108 | 3.824 | 120 | 3.837
76.5 | 0.08 | 85 | 0.098 | 78.3 | 0.223 | 87 | 0.237 | 81.9 | 0.374 | 91 | 0.391 | 85.5 | 0.836 | 95 | 0.85 | 90.9 | 2.035 | 101 | 2.05 | 99.9 | 2.848 | 111 | 2.862 | 108.9 | 3.756 | 121 | 3.768
77.4 | 0.079 | 86 | 0.093 | 79.2 | 0.217 | 88 | 0.233 | 82.8 | 0.367 | 92 | 0.383 | 86.4 | 0.82 | 96 | 0.835 | 91.8 | 1.991 | 102 | 2.008 | 100.8 | 2.802 | 112 | 2.816 | 109.8 | 3.687 | 122 | 3.702
78.3 | 0.077 | 87 | 0.093 | 80.1 | 0.211 | 89 | 0.225 | 83.7 | 0.359 | 93 | 0.375 | 87.3 | 0.805 | 97 | 0.818 | 92.7 | 1.947 | 103 | 1.96 | 101.7 | 2.756 | 113 | 2.771 | 110.7 | 3.619 | 123 | 3.633
79.2 | 0.076 | 88 | 0.091 | 81 | 0.208 | 90 | 0.225 | 84.6 | 0.352 | 94 | 0.366 | 88.2 | 0.789 | 98 | 0.804 | 93.6 | 1.904 | 104 | 1.918 | 102.6 | 2.71 | 114 | 2.725 | 111.6 | 3.551 | 124 | 3.566
80.1 | 0.074 | 89 | 0.091 | 81.9 | 0.204 | 91 | 0.218 | 85.5 | 0.345 | 95 | 0.358 | 89.1 | 0.774 | 99 | 0.791 | 94.5 | 1.86 | 105 | 1.875 | 103.5 | 2.664 | 115 | 2.679 | 112.5 | 3.483 | 125 | 3.5
81 | 0.073 | 90 | 0.09 | 82.8 | 0.2 | 92 | 0.216 | 86.4 | 0.337 | 96 | 0.352 | 90 | 0.759 | 100 | 0.775 | 95.4 | 1.816 | 106 | 1.833 | 104.4 | 2.618 | 116 | 2.633 | 113.4 | 3.423 | 126 | 3.437
81.9 | 0.071 | 91 | 0.086 | 83.7 | 0.196 | 93 | 0.21 | 87.3 | 0.33 | 97 | 0.343 | 90.9 | 0.743 | 101 | 0.758 | 96.3 | 1.772 | 107 | 1.785 | 105.3 | 2.572 | 117 | 2.585 | 114.3 | 3.364 | 127 | 3.377
82.8 | 0.07 | 92 | 0.085 | 84.6 | 0.192 | 94 | 0.208 | 88.2 | 0.323 | 98 | 0.337 | 91.8 | 0.728 | 102 | 0.741 | 97.2 | 1.729 | 108 | 1.743 | 106.2 | 2.526 | 118 | 2.541 | 115.2 | 3.305 | 128 | 3.318
83.7 | 0.068 | 93 | 0.084 | 85.5 | 0.189 | 95 | 0.206 | 89.1 | 0.315 | 99 | 0.329 | 92.7 | 0.712 | 103 | 0.727 | 98.1 | 1.692 | 109 | 1.708 | 107.1 | 2.48 | 119 | 2.493 | 116.1 | 3.245 | 129 | 3.26
84.6 | 0.067 | 94 | 0.083 | 86.4 | 0.185 | 96 | 0.201 | 90 | 0.308 | 100 | 0.325 | 93.6 | 0.697 | 104 | 0.71 | 99 | 1.655 | 110 | 1.668 | 108 | 2.435 | 120 | 2.45 | 117 | 3.186 | 130 | 3.2
85.5 | 0.065 | 95 | 0.083 | 87.3 | 0.181 | 97 | 0.198 | 90.9 | 0.3 | 101 | 0.316 | 94.5 | 0.682 | 105 | 0.696 | 99.9 | 1.619 | 111 | 1.633 | 108.9 | 2.389 | 121 | 2.402 | 117.9 | 3.127 | 131 | 3.141
86.4 | 0.064 | 96 | 0.078 | 88.2 | 0.178 | 98 | 0.193 | 91.8 | 0.293 | 102 | 0.308 | 95.4 | 0.666 | 106 | 0.683 | 100.8 | 1.582 | 112 | 1.596 | 109.8 | 2.356 | 122 | 2.368 | 118.8 | 3.067 | 132 | 3.083
87.3 | 0.06 | 97 | 0.076 | 89.1 | 0.174 | 99 | 0.191 | 92.7 | 0.286 | 103 | 0.3 | 96.3 | 0.651 | 107 | 0.666 | 101.7 | 1.545 | 113 | 1.56 | 110.7 | 2.323 | 123 | 2.337 | 119.7 | 3.008 | 133 | 3.025
88.2 | 0.056 | 98 | 0.069 | 90 | 0.17 | 100 | 0.185 | 93.6 | 0.282 | 104 | 0.296 | 97.2 | 0.641 | 108 | 0.658 | 102.6 | 1.509 | 114 | 1.525 | 111.6 | 2.29 | 124 | 2.304 | 120.6 | 2.966 | 134 | 2.983
89.1 | 0.052 | 99 | 0.068 | 90.9 | 0.167 | 101 | 0.183 | 94.5 | 0.278 | 105 | 0.291 | 98.1 | 0.632 | 109 | 0.646 | 103.5 | 1.472 | 115 | 1.485 | 112.5 | 2.257 | 125 | 2.271 | 121.5 | 2.924 | 135 | 2.941
90 | 0.048 | 100 | 0.065 | 91.8 | 0.164 | 102 | 0.181 | 95.4 | 0.274 | 106 | 0.291 | 99 | 0.622 | 110 | 0.635 | 104.4 | 1.435 | 116 | 1.45 | 113.4 | 2.224 | 126 | 2.237 | 122.4 | 2.882 | 136 | 2.896
90.9 | 0.044 | 101 | 0.06 | 92.7 | 0.161 | 103 | 0.176 | 96.3 | 0.27 | 107 | 0.285 | 99.9 | 0.612 | 111 | 0.627 | 105.3 | 1.399 | 117 | 1.412 | 114.3 | 2.19 | 127 | 2.208 | 123.3 | 2.84 | 137 | 2.854
189 | 0.036 | 500 | 0.05 | 93.6 | 0.158 | 104 | 0.175 | 97.2 | 0.266 | 108 | 0.283 | 100.8 | 0.603 | 112 | 0.616 | 106.2 | 1.362 | 118 | 1.377 | 115.2 | 2.157 | 128 | 2.175 | 124.2 | 2.798 | 138 | 2.812
250.2 | 0.035 | 500 | 0.033 | 94.5 | 0.155 | 105 | 0.169 | 98.1 | 0.262 | 109 | 0.277 | 101.7 | 0.593 | 113 | 0.608 | 107.1 | 1.337 | 119 | 1.352 | 116.1 | 2.124 | 129 | 2.141 | 125.1 | 2.756 | 139 | 2.771
250.2 | 0.007 | 1000 | 0.033 | 95.4 | 0.153 | 106 | 0.168 | 99 | 0.258 | 110 | 0.275 | 102.6 | 0.583 | 114 | 0.6 | 108 | 1.312 | 120 | 1.327 | 117 | 2.091 | 130 | 2.108 | 126 | 2.714 | 140 | 2.729
468 | 0.003 | 6300 | 0.022 | 96.3 | 0.15 | 107 | 0.166 | 99.9 | 0.254 | 111 | 0.268 | 103.5 | 0.574 | 115 | 0.587 | 108.9 | 1.288 | 121 | 1.302 | 117.9 | 2.058 | 131 | 2.075 | 126.9 | 2.672 | 141 | 2.685
6300 | 0.003 |  |  | 97.2 | 0.147 | 108 | 0.161 | 100.8 | 0.25 | 112 | 0.266 | 104.4 | 0.564 | 116 | 0.579 | 109.8 | 1.263 | 122 | 1.277 | 118.8 | 2.025 | 132 | 2.041 | 127.8 | 2.63 | 142 | 2.643
|  |  |  | 98.1 | 0.144 | 109 | 0.159 | 101.7 | 0.246 | 113 | 0.26 | 105.3 | 0.555 | 117 | 0.568 | 110.7 | 1.238 | 123 | 1.252 | 119.7 | 1.992 | 133 | 2.008 | 128.7 | 2.589 | 143 | 2.602
|  |  |  | 99 | 0.141 | 110 | 0.158 | 102.6 | 0.243 | 114 | 0.258 | 106.2 | 0.545 | 118 | 0.56 | 111.6 | 1.213 | 124 | 1.227 | 120.6 | 1.967 | 134 | 1.983 | 129.6 | 2.547 | 144 | 2.56
|  |  |  | 99.9 | 0.139 | 111 | 0.152 | 103.5 | 0.239 | 115 | 0.252 | 107.1 | 0.535 | 119 | 0.55 | 112.5 | 1.188 | 125 | 1.202 | 121.5 | 1.943 | 135 | 1.958 | 130.5 | 2.516 | 145 | 2.533
|  |  |  | 100.8 | 0.136 | 112 | 0.151 | 104.4 | 0.235 | 116 | 0.25 | 108 | 0.526 | 120 | 0.541 | 113.4 | 1.164 | 126 | 1.177 | 122.4 | 1.918 | 136 | 1.933 | 131.4 | 2.485 | 146 | 2.5
|  |  |  | 101.7 | 0.133 | 113 | 0.15 | 105.3 | 0.231 | 117 | 0.246 | 108.9 | 0.516 | 121 | 0.533 | 114.3 | 1.139 | 127 | 1.152 | 123.3 | 1.893 | 137 | 1.908 | 132.3 | 2.455 | 147 | 2.468
|  |  |  | 102.6 | 0.131 | 114 | 0.148 | 106.2 | 0.227 | 118 | 0.241 | 109.8 | 0.506 | 122 | 0.521 | 115.2 | 1.114 | 128 | 1.127 | 124.2 | 1.868 | 138 | 1.883 | 133.2 | 2.424 | 148 | 2.441
|  |  |  | 103.5 | 0.129 | 115 | 0.144 | 107.1 | 0.223 | 119 | 0.237 | 110.7 | 0.497 | 123 | 0.51 | 116.1 | 1.089 | 129 | 1.104 | 125.1 | 1.843 | 139 | 1.858 | 134.1 | 2.393 | 149 | 2.408
|  |  |  | 104.4 | 0.128 | 116 | 0.143 | 108 | 0.219 | 120 | 0.233 | 111.6 | 0.487 | 124 | 0.502 | 117 | 1.065 | 130 | 1.079 | 126 | 1.818 | 140 | 1.833 | 135 | 2.363 | 150 | 2.377
|  |  |  | 105.3 | 0.126 | 117 | 0.141 | 108.9 | 0.215 | 121 | 0.229 | 112.5 | 0.478 | 125 | 0.491 | 117.9 | 1.04 | 131 | 1.054 | 126.9 | 1.793 | 141 | 1.808 | 135.9 | 2.332 | 151 | 2.346
|  |  |  | 106.2 | 0.124 | 118 | 0.141 | 109.8 | 0.211 | 122 | 0.225 | 113.4 | 0.472 | 126 | 0.485 | 118.8 | 1.026 | 132 | 1.041 | 127.8 | 1.768 | 142 | 1.783 | 136.8 | 2.301 | 152 | 2.316
|  |  |  | 107.1 | 0.122 | 119 | 0.139 | 110.7 | 0.208 | 123 | 0.225 | 114.3 | 0.466 | 127 | 0.483 | 119.7 | 1.011 | 133 | 1.027 | 128.7 | 1.744 | 143 | 1.758 | 137.7 | 2.271 | 153 | 2.285
|  |  |  | 108 | 0.12 | 120 | 0.135 | 111.6 | 0.204 | 124 | 0.218 | 115.2 | 0.46 | 128 | 0.475 | 120.6 | 0.997 | 134 | 1.01 | 129.6 | 1.719 | 144 | 1.733 | 138.6 | 2.24 | 154 | 2.254
|  |  |  | 108.9 | 0.118 | 121 | 0.134 | 112.5 | 0.2 | 125 | 0.216 | 116.1 | 0.454 | 129 | 0.468 | 121.5 | 0.983 | 135 | 1 | 130.5 | 1.694 | 145 | 1.708 | 139.5 | 2.209 | 155 | 2.225
|  |  |  | 109.8 | 0.117 | 122 | 0.133 | 113.4 | 0.196 | 126 | 0.21 | 117 | 0.448 | 130 | 0.462 | 122.4 | 0.969 | 136 | 0.983 | 131.4 | 1.669 | 146 | 1.683 | 140.4 | 2.179 | 156 | 2.193
|  |  |  | 110.7 | 0.115 | 123 | 0.132 | 114.3 | 0.192 | 127 | 0.208 | 117.9 | 0.442 | 131 | 0.458 | 123.3 | 0.955 | 137 | 0.968 | 132.3 | 1.648 | 147 | 1.662 | 141.3 | 2.148 | 157 | 2.162
|  |  |  | 111.6 | 0.113 | 124 | 0.127 | 115.2 | 0.188 | 128 | 0.202 | 118.8 | 0.437 | 132 | 0.452 | 124.2 | 0.94 | 138 | 0.958 | 133.2 | 1.626 | 148 | 1.641 | 142.2 | 2.117 | 158 | 2.133
|  |  |  | 112.5 | 0.111 | 125 | 0.127 | 116.1 | 0.186 | 129 | 0.201 | 119.7 | 0.431 | 133 | 0.446 | 125.1 | 0.926 | 139 | 0.941 | 134.1 | 1.605 | 149 | 1.618 | 143.1 | 2.087 | 159 | 2.102
|  |  |  | 113.4 | 0.109 | 126 | 0.125 | 117 | 0.184 | 130 | 0.2 | 120.6 | 0.425 | 134 | 0.441 | 126 | 0.912 | 140 | 0.927 | 135 | 1.584 | 150 | 1.6 | 144 | 2.056 | 160 | 2.071
|  |  |  | 114.3 | 0.108 | 127 | 0.125 | 117.9 | 0.182 | 131 | 0.198 | 121.5 | 0.419 | 135 | 0.433 | 126.9 | 0.898 | 141 | 0.912 | 135.9 | 1.562 | 151 | 1.577 | 144.9 | 2.025 | 161 | 2.041
|  |  |  | 115.2 | 0.106 | 128 | 0.123 | 118.8 | 0.18 | 132 | 0.194 | 122.4 | 0.413 | 136 | 0.427 | 127.8 | 0.884 | 142 | 0.9 | 136.8 | 1.541 | 152 | 1.558 | 145.8 | 2.004 | 162 | 2.018
|  |  |  | 116.1 | 0.105 | 129 | 0.119 | 119.7 | 0.177 | 133 | 0.193 | 123.3 | 0.407 | 137 | 0.425 | 128.7 | 0.87 | 143 | 0.883 | 137.7 | 1.52 | 153 | 1.535 | 146.7 | 1.982 | 163 | 2
|  |  |  | 117 | 0.104 | 130 | 0.118 | 120.6 | 0.175 | 134 | 0.191 | 124.2 | 0.401 | 138 | 0.416 | 129.6 | 0.855 | 144 | 0.868 | 138.6 | 1.499 | 154 | 1.512 | 147.6 | 1.961 | 164 | 1.975
|  |  |  | 117.9 | 0.102 | 131 | 0.118 | 121.5 | 0.173 | 135 | 0.19 | 125.1 | 0.396 | 139 | 0.41 | 130.5 | 0.841 | 145 | 0.858 | 139.5 | 1.477 | 155 | 1.491 | 148.5 | 1.939 | 165 | 1.954
|  |  |  | 118.8 | 0.101 | 132 | 0.116 | 122.4 | 0.171 | 136 | 0.186 | 126 | 0.39 | 140 | 0.404 | 131.4 | 0.827 | 146 | 0.841 | 140.4 | 1.456 | 156 | 1.471 | 149.4 | 1.918 | 166 | 1.933
|  |  |  | 119.7 | 0.1 | 133 | 0.116 | 123.3 | 0.169 | 137 | 0.184 | 126.9 | 0.384 | 141 | 0.4 | 132.3 | 0.813 | 147 | 0.827 | 141.3 | 1.435 | 157 | 1.45 | 150.3 | 1.896 | 167 | 1.91
|  |  |  | 120.6 | 0.099 | 134 | 0.116 | 124.2 | 0.167 | 138 | 0.183 | 127.8 | 0.378 | 142 | 0.391 | 133.2 | 0.799 | 148 | 0.816 | 142.2 | 1.413 | 158 | 1.427 | 151.2 | 1.875 | 168 | 1.891
|  |  |  | 121.5 | 0.097 | 135 | 0.115 | 125.1 | 0.165 | 139 | 0.182 | 128.7 | 0.372 | 143 | 0.385 | 134.1 | 0.785 | 149 | 0.8 | 143.1 | 1.392 | 159 | 1.408 | 152.1 | 1.853 | 169 | 1.866
|  |  |  | 122.4 | 0.096 | 136 | 0.111 | 126 | 0.163 | 140 | 0.177 | 129.6 | 0.366 | 144 | 0.383 | 135 | 0.776 | 150 | 0.791 | 144 | 1.371 | 160 | 1.385 | 153 | 1.832 | 170 | 1.846
|  |  |  | 123.3 | 0.095 | 137 | 0.11 | 126.9 | 0.161 | 141 | 0.176 | 130.5 | 0.361 | 145 | 0.375 | 135.9 | 0.766 | 151 | 0.783 | 144.9 | 1.35 | 161 | 1.366 | 153.9 | 1.81 | 171 | 1.825
|  |  |  | 124.2 | 0.094 | 138 | 0.109 | 127.8 | 0.159 | 142 | 0.175 | 131.4 | 0.357 | 146 | 0.371 | 136.8 | 0.757 | 152 | 0.775 | 145.8 | 1.328 | 162 | 1.343 | 154.8 | 1.788 | 172 | 1.802
|  |  |  | 125.1 | 0.092 | 139 | 0.108 | 128.7 | 0.157 | 143 | 0.175 | 132.3 | 0.353 | 147 | 0.366 | 137.7 | 0.748 | 153 | 0.762 | 146.7 | 1.312 | 163 | 1.327 | 155.7 | 1.767 | 173 | 1.783
|  |  |  | 126 | 0.091 | 140 | 0.108 | 129.6 | 0.155 | 144 | 0.169 | 133.2 | 0.349 | 148 | 0.366 | 138.6 | 0.739 | 154 | 0.752 | 147.6 | 1.296 | 164 | 1.31 | 156.6 | 1.745 | 174 | 1.76
|  |  |  | 126.9 | 0.09 | 141 | 0.107 | 130.5 | 0.153 | 145 | 0.168 | 134.1 | 0.345 | 149 | 0.36 | 139.5 | 0.73 | 155 | 0.743 | 148.5 | 1.279 | 165 | 1.293 | 157.5 | 1.724 | 175 | 1.741
|  |  |  | 127.8 | 0.088 | 142 | 0.102 | 131.4 | 0.151 | 146 | 0.166 | 135 | 0.341 | 150 | 0.358 | 140.4 | 0.721 | 156 | 0.735 | 149.4 | 1.263 | 166 | 1.277 | 158.4 | 1.702 | 176 | 1.716
|  |  |  | 128.7 | 0.087 | 143 | 0.102 | 132.3 | 0.149 | 147 | 0.166 | 135.9 | 0.337 | 151 | 0.352 | 141.3 | 0.711 | 157 | 0.725 | 150.3 | 1.246 | 167 | 1.26 | 159.3 | 1.681 | 177 | 1.696
|  |  |  | 129.6 | 0.085 | 144 | 0.101 | 133.2 | 0.147 | 148 | 0.161 | 136.8 | 0.333 | 152 | 0.35 | 142.2 | 0.702 | 158 | 0.716 | 151.2 | 1.23 | 168 | 1.243 | 160.2 | 1.659 | 178 | 1.675
|  |  |  | 130.5 | 0.078 | 145 | 0.094 | 134.1 | 0.145 | 149 | 0.16 | 137.7 | 0.33 | 153 | 0.343 | 143.1 | 0.693 | 159 | 0.708 | 152.1 | 1.213 | 169 | 1.227 | 161.1 | 1.638 | 179 | 1.652
|  |  |  | 131.4 | 0.071 | 146 | 0.086 | 135 | 0.143 | 150 | 0.158 | 138.6 | 0.326 | 154 | 0.341 | 144 | 0.684 | 160 | 0.7 | 153 | 1.197 | 170 | 1.21 | 162 | 1.616 | 180 | 1.633
|  |  |  | 132.3 | 0.064 | 147 | 0.082 | 135.9 | 0.141 | 151 | 0.158 | 139.5 | 0.322 | 155 | 0.335 | 144.9 | 0.675 | 161 | 0.691 | 153.9 | 1.181 | 171 | 1.193 | 162.9 | 1.595 | 181 | 1.61
|  |  |  | 133.2 | 0.057 | 148 | 0.075 | 136.8 | 0.139 | 152 | 0.152 | 140.4 | 0.318 | 156 | 0.333 | 145.8 | 0.666 | 162 | 0.683 | 154.8 | 1.164 | 172 | 1.179 | 163.8 | 1.573 | 182 | 1.587
|  |  |  | 134.1 | 0.051 | 149 | 0.068 | 137.7 | 0.137 | 153 | 0.152 | 141.3 | 0.314 | 157 | 0.329 | 146.7 | 0.657 | 163 | 0.671 | 155.7 | 1.148 | 173 | 1.162 | 164.7 | 1.552 | 183 | 1.566
|  |  |  | 135 | 0.045 | 150 | 0.061 | 138.6 | 0.135 | 154 | 0.15 | 142.2 | 0.31 | 158 | 0.325 | 147.6 | 0.647 | 164 | 0.662 | 156.6 | 1.131 | 174 | 1.146 | 165.6 | 1.53 | 184 | 1.543
|  |  |  | 135.9 | 0.045 | 500 | 0.05 | 139.5 | 0.133 | 155 | 0.15 | 143.1 | 0.306 | 159 | 0.321 | 148.5 | 0.638 | 165 | 0.652 | 157.5 | 1.115 | 175 | 1.129 | 166.5 | 1.509 | 185 | 1.525
|  |  |  | 136.8 | 0.044 | 500 | 0.033 | 140.4 | 0.131 | 156 | 0.148 | 144 | 0.303 | 160 | 0.316 | 149.4 | 0.629 | 166 | 0.643 | 158.4 | 1.099 | 176 | 1.112 | 167.4 | 1.493 | 186 | 1.508
|  |  |  | 137.7 | 0.044 | 1000 | 0.033 | 141.3 | 0.13 | 157 | 0.144 | 144.9 | 0.299 | 161 | 0.312 | 150.3 | 0.62 | 167 | 0.635 | 159.3 | 1.086 | 177 | 1.1 | 168.3 | 1.478 | 187 | 1.491
|  |  |  | 138.6 | 0.044 | 6300 | 0.022 | 142.2 | 0.128 | 158 | 0.143 | 145.8 | 0.295 | 162 | 0.31 | 151.2 | 0.611 | 168 | 0.625 | 160.2 | 1.074 | 178 | 1.087 | 169.2 | 1.462 | 188 | 1.477
|  |  |  | 139.5 | 0.044 |  |  | 143.1 | 0.127 | 159 | 0.143 | 146.7 | 0.291 | 163 | 0.308 | 152.1 | 0.602 | 169 | 0.616 | 161.1 | 1.061 | 179 | 1.075 | 170.1 | 1.447 | 189 | 1.46
|  |  |  | 140.4 | 0.044 |  |  | 144 | 0.126 | 160 | 0.141 | 147.6 | 0.287 | 164 | 0.302 | 153 | 0.593 | 170 | 0.608 | 162 | 1.048 | 180 | 1.062 | 171 | 1.431 | 190 | 1.446
|  |  |  | 141.3 | 0.044 |  |  | 144.9 | 0.125 | 161 | 0.141 | 148.5 | 0.283 | 165 | 0.3 | 153.9 | 0.583 | 171 | 0.6 | 162.9 | 1.036 | 181 | 1.05 | 171.9 | 1.416 | 191 | 1.433
|  |  |  | 142.2 | 0.044 |  |  | 145.8 | 0.124 | 162 | 0.141 | 149.4 | 0.279 | 166 | 0.293 | 154.8 | 0.574 | 172 | 0.591 | 163.8 | 1.023 | 182 | 1.037 | 172.8 | 1.401 | 192 | 1.416
|  |  |  | 143.1 | 0.044 |  |  | 146.7 | 0.123 | 163 | 0.14 | 150.3 | 0.276 | 167 | 0.291 | 155.7 | 0.569 | 173 | 0.583 | 164.7 | 1.011 | 183 | 1.025 | 173.7 | 1.385 | 193 | 1.4
|  |  |  | 144 | 0.044 |  |  | 147.6 | 0.122 | 164 | 0.136 | 151.2 | 0.272 | 168 | 0.285 | 156.6 | 0.564 | 174 | 0.577 | 165.6 | 0.998 | 184 | 1.012 | 174.6 | 1.37 | 194 | 1.383
|  |  |  | 144.9 | 0.044 |  |  | 148.5 | 0.121 | 165 | 0.135 | 152.1 | 0.268 | 169 | 0.283 | 157.5 | 0.558 | 175 | 0.575 | 166.5 | 0.986 | 185 | 1 | 175.5 | 1.354 | 195 | 1.368
|  |  |  | 145.8 | 0.044 |  |  | 149.4 | 0.12 | 166 | 0.135 | 153 | 0.264 | 170 | 0.277 | 158.4 | 0.553 | 176 | 0.566 | 167.4 | 0.973 | 186 | 0.987 | 176.4 | 1.339 | 196 | 1.352
|  |  |  | 146.7 | 0.043 |  |  | 150.3 | 0.118 | 167 | 0.134 | 153.9 | 0.26 | 171 | 0.275 | 159.3 | 0.547 | 177 | 0.56 | 168.3 | 0.96 | 187 | 0.975 | 177.3 | 1.323 | 197 | 1.337
|  |  |  | 147.6 | 0.043 |  |  | 151.2 | 0.117 | 168 | 0.133 | 154.8 | 0.258 | 172 | 0.275 | 160.2 | 0.542 | 178 | 0.558 | 169.2 | 0.948 | 188 | 0.962 | 178.2 | 1.308 | 198 | 1.325
|  |  |  | 148.5 | 0.043 |  |  | 152.1 | 0.116 | 169 | 0.133 | 155.7 | 0.256 | 173 | 0.271 | 161.1 | 0.536 | 179 | 0.552 | 170.1 | 0.935 | 189 | 0.95 | 179.1 | 1.297 | 199 | 1.31
|  |  |  | 149.4 | 0.043 |  |  | 153 | 0.115 | 170 | 0.132 | 156.6 | 0.254 | 174 | 0.268 | 162 | 0.531 | 180 | 0.546 | 171 | 0.923 | 190 | 0.937 | 180 | 1.286 | 200 | 1.3
|  |  |  | 150.3 | 0.043 |  |  | 153.9 | 0.114 | 171 | 0.132 | 157.5 | 0.251 | 175 | 0.266 | 162.9 | 0.526 | 181 | 0.541 | 171.9 | 0.91 | 191 | 0.925 | 180.9 | 1.275 | 201 | 1.291
|  |  |  | 151.2 | 0.043 |  |  | 154.8 | 0.113 | 172 | 0.127 | 158.4 | 0.249 | 176 | 0.266 | 163.8 | 0.52 | 182 | 0.535 | 172.8 | 0.898 | 192 | 0.912 | 181.8 | 1.264 | 202 | 1.277
|  |  |  | 152.1 | 0.043 |  |  | 155.7 | 0.112 | 173 | 0.127 | 159.3 | 0.247 | 177 | 0.26 | 164.7 | 0.515 | 183 | 0.529 | 173.7 | 0.885 | 193 | 0.9 | 182.7 | 1.253 | 203 | 1.266
|  |  |  | 153 | 0.043 |  |  | 156.6 | 0.111 | 174 | 0.126 | 160.2 | 0.245 | 178 | 0.258 | 165.6 | 0.509 | 184 | 0.525 | 174.6 | 0.873 | 194 | 0.887 | 183.6 | 1.242 | 204 | 1.258
|  |  |  | 153.9 | 0.043 |  |  | 157.5 | 0.11 | 175 | 0.125 | 161.1 | 0.242 | 179 | 0.258 | 166.5 | 0.504 | 185 | 0.518 | 175.5 | 0.86 | 195 | 0.875 | 184.5 | 1.231 | 205 | 1.243
|  |  |  | 154.8 | 0.043 |  |  | 158.4 | 0.109 | 176 | 0.125 | 162 | 0.24 | 180 | 0.254 | 167.4 | 0.499 | 186 | 0.512 | 176.4 | 0.847 | 196 | 0.86 | 185.4 | 1.22 | 206 | 1.233
|  |  |  | 155.7 | 0.043 |  |  | 159.3 | 0.108 | 177 | 0.125 | 162.9 | 0.238 | 181 | 0.252 | 168.3 | 0.493 | 187 | 0.508 | 177.3 | 0.835 | 197 | 0.85 | 186.3 | 1.209 | 207 | 1.225
|  |  |  | 156.6 | 0.043 |  |  | 160.2 | 0.106 | 178 | 0.123 | 163.8 | 0.236 | 182 | 0.25 | 169.2 | 0.488 | 188 | 0.502 | 178.2 | 0.822 | 198 | 0.835 | 187.2 | 1.198 | 208 | 1.212
|  |  |  | 157.5 | 0.043 |  |  | 161.1 | 0.105 | 179 | 0.119 | 164.7 | 0.233 | 183 | 0.25 | 170.1 | 0.482 | 189 | 0.5 | 179.1 | 0.81 | 199 | 0.825 | 188.1 | 1.187 | 209 | 1.202
|  |  |  | 158.4 | 0.043 |  |  | 162 | 0.104 | 180 | 0.119 | 165.6 | 0.231 | 184 | 0.246 | 171 | 0.477 | 190 | 0.491 | 180 | 0.802 | 200 | 0.816 | 189 | 1.176 | 210 | 1.191
|  |  |  | 159.3 | 0.043 |  |  | 162.9 | 0.103 | 181 | 0.118 | 166.5 | 0.229 | 185 | 0.243 | 171.9 | 0.472 | 191 | 0.485 | 180.9 | 0.795 | 201 | 0.81 | 189.9 | 1.165 | 211 | 1.179
|  |  |  | 160.2 | 0.043 |  |  | 163.8 | 0.102 | 182 | 0.118 | 167.4 | 0.227 | 186 | 0.241 | 172.8 | 0.466 | 192 | 0.483 | 181.8 | 0.787 | 202 | 0.802 | 190.8 | 1.154 | 212 | 1.168
|  |  |  | 161.1 | 0.043 |  |  | 164.7 | 0.101 | 183 | 0.116 | 168.3 | 0.225 | 187 | 0.241 | 173.7 | 0.461 | 193 | 0.475 | 182.7 | 0.78 | 203 | 0.793 | 191.7 | 1.143 | 213 | 1.158
|  |  |  | 162 | 0.043 |  |  | 165.6 | 0.1 | 184 | 0.116 | 169.2 | 0.222 | 188 | 0.237 | 174.6 | 0.455 | 194 | 0.468 | 183.6 | 0.772 | 204 | 0.785 | 192.6 | 1.131 | 214 | 1.146
|  |  |  | 162.9 | 0.042 |  |  | 166.5 | 0.099 | 185 | 0.116 | 170.1 | 0.22 | 189 | 0.235 | 175.5 | 0.45 | 195 | 0.466 | 184.5 | 0.765 | 205 | 0.779 | 193.5 | 1.12 | 215 | 1.135
|  |  |  | 163.8 | 0.042 |  |  | 167.4 | 0.098 | 186 | 0.115 | 171 | 0.218 | 190 | 0.233 | 176.4 | 0.445 | 196 | 0.458 | 185.4 | 0.757 | 206 | 0.775 | 194.4 | 1.109 | 216 | 1.125
|  |  |  | 164.7 | 0.042 |  |  | 168.3 | 0.097 | 187 | 0.111 | 171.9 | 0.216 | 191 | 0.233 | 177.3 | 0.439 | 197 | 0.454 | 186.3 | 0.75 | 207 | 0.766 | 195.3 | 1.098 | 217 | 1.112
|  |  |  | 165.6 | 0.042 |  |  | 169.2 | 0.096 | 188 | 0.11 | 172.8 | 0.214 | 192 | 0.227 | 178.2 | 0.436 | 198 | 0.45 | 187.2 | 0.742 | 208 | 0.758 | 196.2 | 1.087 | 218 | 1.102
|  |  |  | 166.5 | 0.042 |  |  | 170.1 | 0.094 | 189 | 0.11 | 173.7 | 0.211 | 193 | 0.225 | 179.1 | 0.432 | 199 | 0.45 | 188.1 | 0.735 | 209 | 0.75 | 197.1 | 1.076 | 219 | 1.091
|  |  |  | 167.4 | 0.042 |  |  | 171 | 0.093 | 190 | 0.109 | 174.6 | 0.209 | 194 | 0.225 | 180 | 0.429 | 200 | 0.443 | 189 | 0.727 | 210 | 0.741 | 198 | 1.065 | 220 | 1.083
|  |  |  | 168.3 | 0.042 |  |  | 171.9 | 0.092 | 191 | 0.108 | 175.5 | 0.207 | 195 | 0.221 | 180.9 | 0.426 | 201 | 0.441 | 189.9 | 0.72 | 211 | 0.735 | 198.9 | 1.054 | 221 | 1.068
|  |  |  | 169.2 | 0.042 |  |  | 172.8 | 0.091 | 192 | 0.108 | 176.4 | 0.205 | 196 | 0.218 | 181.8 | 0.422 | 202 | 0.435 | 190.8 | 0.713 | 212 | 0.727 | 199.8 | 1.043 | 222 | 1.058
|  |  |  | 170.1 | 0.042 |  |  | 173.7 | 0.09 | 193 | 0.107 | 177.3 | 0.203 | 197 | 0.216 | 182.7 | 0.419 | 203 | 0.433 | 191.7 | 0.705 | 213 | 0.718 | 200.7 | 1.032 | 223 | 1.05
|  |  |  | 171 | 0.042 |  |  | 174.6 | 0.089 | 194 | 0.107 | 178.2 | 0.2 | 198 | 0.216 | 183.6 | 0.415 | 204 | 0.429 | 192.6 | 0.698 | 214 | 0.712 | 201.6 | 1.021 | 224 | 1.035
|  |  |  | 171.9 | 0.042 |  |  | 175.5 | 0.088 | 195 | 0.102 | 179.1 | 0.198 | 199 | 0.212 | 184.5 | 0.412 | 205 | 0.427 | 193.5 | 0.69 | 215 | 0.704 | 202.5 | 1.01 | 225 | 1.025
|  |  |  | 172.8 | 0.042 |  |  | 176.4 | 0.087 | 196 | 0.102 | 180 | 0.196 | 200 | 0.21 | 185.4 | 0.408 | 206 | 0.425 | 194.4 | 0.683 | 216 | 0.7 | 203.4 | 1.003 | 226 | 1.016
|  |  |  | 173.7 | 0.042 |  |  | 177.3 | 0.086 | 197 | 0.101 | 180.9 | 0.193 | 201 | 0.209 | 186.3 | 0.405 | 207 | 0.418 | 195.3 | 0.675 | 217 | 0.691 | 204.3 | 0.995 | 227 | 1.008
|  |  |  | 174.6 | 0.042 |  |  | 178.2 | 0.085 | 198 | 0.101 | 181.8 | 0.191 | 202 | 0.208 | 187.2 | 0.402 | 208 | 0.416 | 196.2 | 0.668 | 218 | 0.683 | 205.2 | 0.987 | 228 | 1.002
|  |  |  | 175.5 | 0.042 |  |  | 179.1 | 0.084 | 199 | 0.1 | 182.7 | 0.189 | 203 | 0.207 | 188.1 | 0.398 | 209 | 0.412 | 197.1 | 0.66 | 219 | 0.675 | 206.1 | 0.979 | 229 | 0.993
|  |  |  | 176.4 | 0.042 |  |  | 180 | 0.084 | 200 | 0.1 | 183.6 | 0.187 | 204 | 0.202 | 189 | 0.395 | 210 | 0.408 | 198 | 0.653 | 220 | 0.666 | 207 | 0.971 | 230 | 0.985
|  |  |  | 177.3 | 0.042 |  |  | 180.9 | 0.083 | 201 | 0.1 | 184.5 | 0.185 | 205 | 0.201 | 189.9 | 0.391 | 211 | 0.408 | 198.9 | 0.647 | 221 | 0.66 | 207.9 | 0.963 | 231 | 0.977
|  |  |  | 178.2 | 0.042 |  |  | 181.8 | 0.083 | 202 | 0.1 | 185.4 | 0.184 | 206 | 0.2 | 190.8 | 0.388 | 212 | 0.402 | 199.8 | 0.642 | 222 | 0.658 | 208.8 | 0.955 | 232 | 0.968
|  |  |  | 179.1 | 0.042 |  |  | 182.7 | 0.082 | 203 | 0.1 | 186.3 | 0.182 | 207 | 0.2 | 191.7 | 0.385 | 213 | 0.4 | 200.7 | 0.636 | 223 | 0.65 | 209.7 | 0.947 | 233 | 0.96
|  |  |  | 180 | 0.042 |  |  | 183.6 | 0.081 | 204 | 0.098 | 187.2 | 0.181 | 208 | 0.198 | 192.6 | 0.381 | 214 | 0.396 | 201.6 | 0.631 | 224 | 0.643 | 210.6 | 0.939 | 234 | 0.954
|  |  |  | 180.9 | 0.042 |  |  | 184.5 | 0.081 | 205 | 0.098 | 188.1 | 0.18 | 209 | 0.194 | 193.5 | 0.378 | 215 | 0.391 | 202.5 | 0.625 | 225 | 0.641 | 211.5 | 0.931 | 235 | 0.946
|  |  |  | 181.8 | 0.042 |  |  | 185.4 | 0.08 | 206 | 0.098 | 189 | 0.178 | 210 | 0.193 | 194.4 | 0.374 | 216 | 0.391 | 203.4 | 0.62 | 226 | 0.633 | 212.4 | 0.924 | 236 | 0.937
|  |  |  | 182.7 | 0.042 |  |  | 186.3 | 0.08 | 207 | 0.094 | 189.9 | 0.177 | 211 | 0.193 | 195.3 | 0.371 | 217 | 0.385 | 204.3 | 0.614 | 227 | 0.627 | 213.3 | 0.916 | 237 | 0.933
|  |  |  | 183.6 | 0.041 |  |  | 187.2 | 0.079 | 208 | 0.094 | 190.8 | 0.175 | 212 | 0.191 | 196.2 | 0.367 | 218 | 0.383 | 205.2 | 0.609 | 228 | 0.625 | 214.2 | 0.908 | 238 | 0.925
|  |  |  | 184.5 | 0.041 |  |  | 188.1 | 0.079 | 209 | 0.093 | 191.7 | 0.174 | 213 | 0.191 | 197.1 | 0.364 | 219 | 0.377 | 206.1 | 0.603 | 229 | 0.616 | 215.1 | 0.9 | 239 | 0.916
|  |  |  | 185.4 | 0.041 |  |  | 189 | 0.078 | 210 | 0.093 | 192.6 | 0.173 | 214 | 0.19 | 198 | 0.361 | 220 | 0.375 | 207 | 0.597 | 230 | 0.612 | 216 | 0.892 | 240 | 0.908
|  |  |  | 186.3 | 0.041 |  |  | 189.9 | 0.078 | 211 | 0.093 | 193.5 | 0.171 | 215 | 0.186 | 198.9 | 0.357 | 221 | 0.371 | 207.9 | 0.592 | 231 | 0.608 | 216.9 | 0.884 | 241 | 0.9
|  |  |  | 187.2 | 0.041 |  |  | 190.8 | 0.077 | 212 | 0.093 | 194.4 | 0.17 | 216 | 0.185 | 199.8 | 0.354 | 222 | 0.368 | 208.8 | 0.586 | 232 | 0.6 | 217.8 | 0.876 | 242 | 0.891
|  |  |  | 188.1 | 0.041 |  |  | 191.7 | 0.077 | 213 | 0.093 | 195.3 | 0.168 | 217 | 0.184 | 200.7 | 0.35 | 223 | 0.366 | 209.7 | 0.581 | 233 | 0.596 | 218.7 | 0.868 | 243 | 0.883
|  |  |  | 189 | 0.041 |  |  | 192.6 | 0.076 | 214 | 0.091 | 196.2 | 0.167 | 218 | 0.183 | 201.6 | 0.347 | 224 | 0.36 | 210.6 | 0.575 | 234 | 0.591 | 219.6 | 0.86 | 244 | 0.875
|  |  |  | 189.9 | 0.041 |  |  | 193.5 | 0.076 | 215 | 0.091 | 197.1 | 0.165 | 219 | 0.183 | 202.5 | 0.344 | 225 | 0.358 | 211.5 | 0.57 | 235 | 0.585 | 220.5 | 0.852 | 245 | 0.866
|  |  |  | 190.8 | 0.041 |  |  | 194.4 | 0.075 | 216 | 0.091 | 198 | 0.164 | 220 | 0.182 | 203.4 | 0.34 | 226 | 0.354 | 212.4 | 0.564 | 236 | 0.579 | 221.4 | 0.845 | 246 | 0.858
|  |  |  | 191.7 | 0.041 |  |  | 195.3 | 0.074 | 217 | 0.091 | 198.9 | 0.163 | 221 | 0.177 | 204.3 | 0.337 | 227 | 0.352 | 213.3 | 0.559 | 237 | 0.575 | 222.3 | 0.837 | 247 | 0.852
|  |  |  | 192.6 | 0.041 |  |  | 196.2 | 0.074 | 218 | 0.091 | 199.8 | 0.161 | 222 | 0.177 | 205.2 | 0.333 | 228 | 0.35 | 214.2 | 0.553 | 238 | 0.568 | 223.2 | 0.829 | 248 | 0.843
|  |  |  | 193.5 | 0.041 |  |  | 197.1 | 0.073 | 219 | 0.09 | 200.7 | 0.16 | 223 | 0.176 | 206.1 | 0.33 | 229 | 0.343 | 215.1 | 0.548 | 239 | 0.562 | 224.1 | 0.821 | 249 | 0.835
|  |  |  | 194.4 | 0.041 |  |  | 198 | 0.073 | 220 | 0.09 | 201.6 | 0.158 | 224 | 0.175 | 207 | 0.327 | 230 | 0.341 | 216 | 0.542 | 240 | 0.558 | 225 | 0.815 | 250 | 0.829
|  |  |  | 195.3 | 0.041 |  |  | 198.9 | 0.072 | 221 | 0.09 | 202.5 | 0.157 | 225 | 0.175 | 207.9 | 0.323 | 231 | 0.337 | 216.9 | 0.537 | 241 | 0.552 | 225.9 | 0.808 | 251 | 0.825
|  |  |  | 196.2 | 0.041 |  |  | 199.8 | 0.072 | 222 | 0.086 | 203.4 | 0.156 | 226 | 0.173 | 208.8 | 0.321 | 232 | 0.335 | 217.8 | 0.531 | 242 | 0.546 | 226.8 | 0.802 | 252 | 0.816
|  |  |  | 197.1 | 0.041 |  |  | 200.7 | 0.071 | 223 | 0.086 | 204.3 | 0.154 | 227 | 0.169 | 209.7 | 0.319 | 233 | 0.333 | 218.7 | 0.526 | 243 | 0.541 | 227.7 | 0.796 | 253 | 0.81
|  |  |  | 198 | 0.041 |  |  | 201.6 | 0.071 | 224 | 0.085 | 205.2 | 0.153 | 228 | 0.168 | 210.6 | 0.316 | 234 | 0.333 | 219.6 | 0.52 | 244 | 0.535 | 228.6 | 0.79 | 254 | 0.804
|  |  |  | 198.9 | 0.041 |  |  | 202.5 | 0.07 | 225 | 0.085 | 206.1 | 0.151 | 229 | 0.168 | 211.5 | 0.314 | 235 | 0.329 | 220.5 | 0.515 | 245 | 0.529 | 229.5 | 0.783 | 255 | 0.8
|  |  |  | 199.8 | 0.041 |  |  | 203.4 | 0.07 | 226 | 0.085 | 207 | 0.15 | 230 | 0.166 | 212.4 | 0.312 | 236 | 0.327 | 221.4 | 0.511 | 246 | 0.525 | 230.4 | 0.777 | 256 | 0.791
|  |  |  | 200.7 | 0.041 |  |  | 204.3 | 0.069 | 227 | 0.084 | 207.9 | 0.149 | 231 | 0.165 | 213.3 | 0.31 | 237 | 0.325 | 222.3 | 0.507 | 247 | 0.525 | 231.3 | 0.771 | 257 | 0.785
|  |  |  | 201.6 | 0.041 |  |  | 205.2 | 0.069 | 228 | 0.084 | 208.8 | 0.147 | 232 | 0.164 | 214.2 | 0.307 | 238 | 0.325 | 223.2 | 0.504 | 248 | 0.518 | 232.2 | 0.765 | 258 | 0.779
|  |  |  | 202.5 | 0.041 |  |  | 206.1 | 0.068 | 229 | 0.083 | 209.7 | 0.146 | 233 | 0.16 | 215.1 | 0.305 | 239 | 0.318 | 224.1 | 0.5 | 249 | 0.516 | 233.1 | 0.758 | 259 | 0.775
|  |  |  | 203.4 | 0.041 |  |  | 207 | 0.068 | 230 | 0.083 | 210.6 | 0.144 | 234 | 0.159 | 216 | 0.303 | 240 | 0.316 | 225 | 0.497 | 250 | 0.51 | 234 | 0.752 | 260 | 0.766
|  |  |  | 204.3 | 0.041 |  |  | 207.9 | 0.067 | 231 | 0.083 | 211.5 | 0.143 | 235 | 0.158 | 216.9 | 0.301 | 241 | 0.316 | 225.9 | 0.493 | 251 | 0.508 | 234.9 | 0.746 | 261 | 0.76
|  |  |  | 205.2 | 0.041 |  |  | 208.8 | 0.066 | 232 | 0.083 | 212.4 | 0.142 | 236 | 0.158 | 217.8 | 0.298 | 242 | 0.312 | 226.8 | 0.49 | 252 | 0.504 | 235.8 | 0.74 | 262 | 0.754
|  |  |  | 206.1 | 0.041 |  |  | 209.7 | 0.066 | 233 | 0.083 | 213.3 | 0.141 | 237 | 0.158 | 218.7 | 0.296 | 243 | 0.31 | 227.7 | 0.486 | 253 | 0.5 | 236.7 | 0.733 | 263 | 0.75
|  |  |  | 207 | 0.041 |  |  | 210.6 | 0.065 | 234 | 0.083 | 214.2 | 0.14 | 238 | 0.157 | 219.6 | 0.294 | 244 | 0.308 | 228.6 | 0.483 | 254 | 0.5 | 237.6 | 0.727 | 264 | 0.741
|  |  |  | 207.9 | 0.041 |  |  | 211.5 | 0.065 | 235 | 0.082 | 215.1 | 0.139 | 239 | 0.157 | 220.5 | 0.292 | 245 | 0.308 | 229.5 | 0.479 | 255 | 0.493 | 238.5 | 0.721 | 265 | 0.735
|  |  |  | 208.8 | 0.041 |  |  | 212.4 | 0.064 | 236 | 0.082 | 216 | 0.138 | 240 | 0.152 | 221.4 | 0.29 | 246 | 0.304 | 230.4 | 0.476 | 256 | 0.491 | 239.4 | 0.715 | 266 | 0.729
|  |  |  | 209.7 | 0.041 |  |  | 213.3 | 0.064 | 237 | 0.082 | 216.9 | 0.137 | 241 | 0.152 | 222.3 | 0.287 | 247 | 0.302 | 231.3 | 0.472 | 257 | 0.485 | 240.3 | 0.709 | 267 | 0.725
|  |  |  | 210.6 | 0.041 |  |  | 214.2 | 0.063 | 238 | 0.078 | 217.8 | 0.137 | 242 | 0.152 | 223.2 | 0.285 | 248 | 0.3 | 232.2 | 0.469 | 258 | 0.483 | 241.2 | 0.704 | 268 | 0.718
|  |  |  | 211.5 | 0.041 |  |  | 215.1 | 0.063 | 239 | 0.078 | 218.7 | 0.136 | 243 | 0.151 | 224.1 | 0.283 | 249 | 0.3 | 233.1 | 0.465 | 259 | 0.479 | 242.1 | 0.699 | 269 | 0.716
|  |  |  | 212.4 | 0.041 |  |  | 216 | 0.062 | 240 | 0.077 | 219.6 | 0.135 | 244 | 0.151 | 225 | 0.281 | 250 | 0.293 | 234 | 0.461 | 260 | 0.477 | 243 | 0.694 | 270 | 0.708
|  |  |  | 213.3 | 0.041 |  |  | 216.9 | 0.062 | 241 | 0.077 | 220.5 | 0.134 | 245 | 0.15 | 225.9 | 0.278 | 251 | 0.293 | 234.9 | 0.458 | 261 | 0.475 | 243.9 | 0.689 | 271 | 0.704
|  |  |  | 214.2 | 0.04 |  |  | 217.8 | 0.061 | 242 | 0.077 | 221.4 | 0.133 | 246 | 0.15 | 226.8 | 0.276 | 252 | 0.291 | 235.8 | 0.454 | 262 | 0.468 | 244.8 | 0.685 | 272 | 0.7
|  |  |  | 215.1 | 0.04 |  |  | 218.7 | 0.061 | 243 | 0.076 | 222.3 | 0.132 | 247 | 0.15 | 227.7 | 0.274 | 253 | 0.287 | 236.7 | 0.451 | 263 | 0.466 | 245.7 | 0.68 | 273 | 0.693
|  |  |  | 216 | 0.04 |  |  | 219.6 | 0.06 | 244 | 0.076 | 223.2 | 0.131 | 248 | 0.148 | 228.6 | 0.272 | 254 | 0.285 | 237.6 | 0.447 | 264 | 0.462 | 246.6 | 0.675 | 274 | 0.691
|  |  |  | 216.9 | 0.04 |  |  | 220.5 | 0.059 | 245 | 0.075 | 224.1 | 0.13 | 249 | 0.144 | 229.5 | 0.269 | 255 | 0.283 | 238.5 | 0.444 | 265 | 0.458 | 247.5 | 0.67 | 275 | 0.685
|  |  |  | 217.8 | 0.04 |  |  | 221.4 | 0.058 | 246 | 0.075 | 225 | 0.129 | 250 | 0.144 | 230.4 | 0.267 | 256 | 0.283 | 239.4 | 0.44 | 266 | 0.454 | 248.4 | 0.665 | 276 | 0.683
|  |  |  | 218.7 | 0.04 |  |  | 222.3 | 0.057 | 247 | 0.075 | 225.9 | 0.128 | 251 | 0.143 | 231.3 | 0.265 | 257 | 0.279 | 240.3 | 0.437 | 267 | 0.452 | 249.3 | 0.661 | 277 | 0.675
|  |  |  | 219.6 | 0.04 |  |  | 223.2 | 0.056 | 248 | 0.075 | 226.8 | 0.128 | 252 | 0.143 | 232.2 | 0.263 | 258 | 0.277 | 241.2 | 0.433 | 268 | 0.45 | 250.2 | 0.656 | 278 | 0.671
|  |  |  | 220.5 | 0.04 |  |  | 224.1 | 0.056 | 249 | 0.075 | 227.7 | 0.127 | 253 | 0.143 | 233.1 | 0.261 | 259 | 0.275 | 242.1 | 0.43 | 269 | 0.443 | 250.2 | 0.007 | 279 | 0.666
|  |  |  | 221.4 | 0.04 |  |  | 225 | 0.044 | 250 | 0.06 | 228.6 | 0.126 | 254 | 0.141 | 234 | 0.258 | 260 | 0.275 | 243 | 0.426 | 270 | 0.441 | 468 | 0.003 | 280 | 0.66
|  |  |  | 222.3 | 0.04 |  |  | 225.9 | 0.044 | 500 | 0.05 | 229.5 | 0.125 | 255 | 0.141 | 234.9 | 0.256 | 261 | 0.271 | 243.9 | 0.423 | 271 | 0.437 | 6300 | 0.003 | 281 | 0.658
|  |  |  | 223.2 | 0.04 |  |  | 226.8 | 0.044 | 500 | 0.033 | 230.4 | 0.124 | 256 | 0.141 | 235.8 | 0.254 | 262 | 0.268 | 244.8 | 0.419 | 272 | 0.433 |  |  | 282 | 0.652
|  |  |  | 224.1 | 0.04 |  |  | 227.7 | 0.044 | 1000 | 0.033 | 231.3 | 0.123 | 257 | 0.14 | 236.7 | 0.252 | 263 | 0.266 | 245.7 | 0.417 | 273 | 0.433 |  |  | 283 | 0.646
|  |  |  | 225 | 0.04 |  |  | 228.6 | 0.043 | 6300 | 0.022 | 232.2 | 0.122 | 258 | 0.139 | 237.6 | 0.25 | 264 | 0.266 | 246.6 | 0.414 | 274 | 0.429 |  |  | 284 | 0.641
|  |  |  | 225.9 | 0.04 |  |  | 229.5 | 0.043 |  |  | 233.1 | 0.121 | 259 | 0.136 | 238.5 | 0.249 | 265 | 0.262 | 247.5 | 0.411 | 275 | 0.427 |  |  | 285 | 0.637
|  |  |  | 226.8 | 0.04 |  |  | 230.4 | 0.043 |  |  | 234 | 0.12 | 260 | 0.135 | 239.4 | 0.247 | 266 | 0.26 | 248.4 | 0.409 | 276 | 0.425 |  |  | 286 | 0.633
|  |  |  | 227.7 | 0.04 |  |  | 231.3 | 0.043 |  |  | 234.9 | 0.119 | 261 | 0.134 | 240.3 | 0.246 | 267 | 0.26 | 249.3 | 0.406 | 277 | 0.421 |  |  | 287 | 0.627
|  |  |  | 228.6 | 0.04 |  |  | 232.2 | 0.043 |  |  | 235.8 | 0.119 | 262 | 0.134 | 241.2 | 0.244 | 268 | 0.258 | 250.2 | 0.404 | 278 | 0.418 |  |  | 288 | 0.625
|  |  |  | 229.5 | 0.04 |  |  | 233.1 | 0.043 |  |  | 236.7 | 0.118 | 263 | 0.133 | 242.1 | 0.243 | 269 | 0.258 | 250.2 | 0.007 | 279 | 0.416 |  |  | 289 | 0.618
|  |  |  | 230.4 | 0.04 |  |  | 234 | 0.043 |  |  | 237.6 | 0.117 | 264 | 0.133 | 243 | 0.241 | 270 | 0.258 | 468 | 0.003 | 280 | 0.412 |  |  | 290 | 0.616
|  |  |  | 231.3 | 0.04 |  |  | 234.9 | 0.043 |  |  | 238.5 | 0.116 | 265 | 0.133 | 243.9 | 0.24 | 271 | 0.254 | 6300 | 0.003 | 281 | 0.41 |  |  | 291 | 0.616
|  |  |  | 232.2 | 0.04 |  |  | 235.8 | 0.043 |  |  | 239.4 | 0.115 | 266 | 0.132 | 244.8 | 0.239 | 272 | 0.252 |  |  | 282 | 0.408 |  |  | 292 | 0.612
|  |  |  | 233.1 | 0.04 |  |  | 236.7 | 0.043 |  |  | 240.3 | 0.114 | 267 | 0.132 | 245.7 | 0.237 | 273 | 0.252 |  |  | 283 | 0.408 |  |  | 293 | 0.61
|  |  |  | 234 | 0.04 |  |  | 237.6 | 0.043 |  |  | 241.2 | 0.113 | 268 | 0.127 | 246.6 | 0.236 | 274 | 0.25 |  |  | 284 | 0.402 |  |  | 294 | 0.608
|  |  |  | 234.9 | 0.04 |  |  | 238.5 | 0.043 |  |  | 242.1 | 0.112 | 269 | 0.127 | 247.5 | 0.234 | 275 | 0.25 |  |  | 285 | 0.4 |  |  | 295 | 0.608
|  |  |  | 235.8 | 0.039 |  |  | 239.4 | 0.043 |  |  | 243 | 0.111 | 270 | 0.127 | 248.4 | 0.233 | 276 | 0.25 |  |  | 286 | 0.4 |  |  | 296 | 0.602
|  |  |  | 236.7 | 0.039 |  |  | 240.3 | 0.043 |  |  | 243.9 | 0.111 | 271 | 0.126 | 249.3 | 0.231 | 277 | 0.246 |  |  | 287 | 0.393 |  |  | 297 | 0.602
|  |  |  | 237.6 | 0.039 |  |  | 241.2 | 0.043 |  |  | 244.8 | 0.11 | 272 | 0.125 | 250.2 | 0.23 | 278 | 0.243 |  |  | 288 | 0.391 |  |  | 298 | 0.6
|  |  |  | 238.5 | 0.039 |  |  | 242.1 | 0.043 |  |  | 245.7 | 0.109 | 273 | 0.125 | 250.2 | 0.007 | 279 | 0.243 |  |  | 289 | 0.391 |  |  | 300 | 0.583
|  |  |  | 239.4 | 0.039 |  |  | 243 | 0.043 |  |  | 246.6 | 0.108 | 274 | 0.125 | 468 | 0.003 | 280 | 0.241 |  |  | 290 | 0.387 |  |  | 300 | 0.062
|  |  |  | 240.3 | 0.039 |  |  | 243.9 | 0.043 |  |  | 247.5 | 0.107 | 275 | 0.125 | 6300 | 0.003 | 281 | 0.241 |  |  | 291 | 0.385 |  |  | 500 | 0.057
|  |  |  | 241.2 | 0.039 |  |  | 244.8 | 0.043 |  |  | 248.4 | 0.107 | 276 | 0.123 |  |  | 282 | 0.241 |  |  | 292 | 0.383 |  |  | 500 | 0.033
|  |  |  | 242.1 | 0.039 |  |  | 245.7 | 0.042 |  |  | 249.3 | 0.106 | 277 | 0.123 |  |  | 283 | 0.237 |  |  | 293 | 0.379 |  |  | 1000 | 0.033
|  |  |  | 243 | 0.039 |  |  | 246.6 | 0.042 |  |  | 250.2 | 0.106 | 278 | 0.123 |  |  | 284 | 0.235 |  |  | 294 | 0.377 |  |  | 6300 | 0.022
|  |  |  | 243.9 | 0.038 |  |  | 247.5 | 0.042 |  |  | 250.2 | 0.007 | 279 | 0.119 |  |  | 285 | 0.235 |  |  | 295 | 0.375
|  |  |  | 244.8 | 0.038 |  |  | 248.4 | 0.042 |  |  | 468 | 0.003 | 280 | 0.119 |  |  | 286 | 0.233 |  |  | 296 | 0.375
|  |  |  | 245.7 | 0.038 |  |  | 249.3 | 0.042 |  |  | 6300 | 0.003 | 281 | 0.118 |  |  | 287 | 0.233 |  |  | 297 | 0.368
|  |  |  | 246.6 | 0.038 |  |  | 250.2 | 0.042 |  |  |  |  | 282 | 0.118 |  |  | 288 | 0.229 |  |  | 298 | 0.366
|  |  |  | 247.5 | 0.038 |  |  | 250.2 | 0.007 |  |  |  |  | 283 | 0.118 |  |  | 289 | 0.227 |  |  | 299 | 0.366
|  |  |  | 248.4 | 0.038 |  |  | 468 | 0.003 |  |  |  |  | 284 | 0.118 |  |  | 290 | 0.227 |  |  | 300 | 0.36
|  |  |  | 249.3 | 0.038 |  |  | 6300 | 0.003 |  |  |  |  | 285 | 0.118 |  |  | 291 | 0.225 |  |  | 301 | 0.358
|  |  |  | 250.2 | 0.038 | [8 empty] | 286 | 0.116 |  |  | 292 | 0.225 |  |  | 301 | 0.06
|  |  |  | 250.2 | 0.007 | [8 empty] | 287 | 0.116 |  |  | 293 | 0.225 |  |  | 500 | 0.057
|  |  |  | 468 | 0.003 | [8 empty] | 288 | 0.116 |  |  | 294 | 0.218 |  |  | 500 | 0.033
|  |  |  | 6300 | 0.003 | [8 empty] | 289 | 0.116 |  |  | 295 | 0.218 |  |  | 1000 | 0.033
[14 empty] | 290 | 0.115 |  |  | 296 | 0.218 |  |  | 6300 | 0.022
[14 empty] | 291 | 0.115 |  |  | 297 | 0.216
[14 empty] | 292 | 0.114 |  |  | 298 | 0.216
[14 empty] | 293 | 0.111 |  |  | 300 | 0.216
[14 empty] | 294 | 0.111 |  |  | 300 | 0.06
[14 empty] | 295 | 0.11 |  |  | 500 | 0.057
[14 empty] | 296 | 0.11 |  |  | 500 | 0.033
[14 empty] | 297 | 0.109 |  |  | 1000 | 0.033
[14 empty] | 298 | 0.109 |  |  | 6300 | 0.022
[14 empty] | 300 | 0.108
[14 empty] | 300 | 0.061
[14 empty] | 500 | 0.057
[14 empty] | 500 | 0.033
[14 empty] | 1000 | 0.033
[14 empty] | 6300 | 0.022

## S&C "T" Speed
S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter
S&C "T" Speed | [11 empty] | S&C "T" Speed | [11 empty] | S&C "T" Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025
Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information.
2T |  |  |  | 3T |  |  |  | 5T |  |  |  | 6T |  |  |  | 8T |  |  |  | 10T |  |  |  | 12T |  |  |  | 15T |  |  |  | 20T
Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s
4 | 10.9397 | 5 | 10.9559 | 6 | 26.3226 | 7 | 26.3393 | 9.9 | 67.1039 | 11 | 67.1191 | 11.7 | 103.196 | 13 | 103.2108 | 15.3 | 111.8391 | 17 | 111.8524 | 18.9 | 654.4898 | 21 | 654.5059 | 25.2 | 1640.0261 | 28 | 1640.0427 | 31.5 | 1147.1847 | 35 | 1147.2011 | 39.6 | 1477.5425 | 44 | 1477.5594
5 | 4.3933 | 6 | 4.408 | 7 | 9.1945 | 8 | 9.2101 | 10.8 | 26.3997 | 12 | 26.4163 | 12.6 | 37.2424 | 14 | 37.258 | 16.2 | 48.2595 | 18 | 48.2747 | 19.8 | 106.5668 | 22 | 106.583 | 26.1 | 146.4226 | 29 | 146.4372 | 32.4 | 188.6067 | 36 | 188.6205 | 40.5 | 243.4371 | 45 | 243.4518
6 | 2.5772 | 7 | 2.5913 | 8 | 5.2961 | 9 | 5.3101 | 11.7 | 15.9139 | 13 | 15.9268 | 13.5 | 22.0872 | 15 | 22.1018 | 17.1 | 30.148 | 19 | 30.1622 | 20.7 | 56.8057 | 23 | 56.8184 | 27 | 75.3733 | 30 | 75.3872 | 33.3 | 101.4462 | 37 | 101.4601 | 41.4 | 131.3168 | 46 | 131.333
7 | 1.7471 | 8 | 1.7601 | 9 | 3.5957 | 10 | 3.6101 | 12.6 | 11.1386 | 14 | 11.1518 | 14.4 | 15.3942 | 16 | 15.408 | 18 | 21.6041 | 20 | 21.6184 | 21.6 | 38.1869 | 24 | 38.2018 | 27.9 | 50.1981 | 31 | 50.2122 | 34.2 | 68.7902 | 38 | 68.8038 | 42.3 | 89.2883 | 47 | 89.3018
8 | 1.2812 | 9 | 1.2955 | 9.9 | 2.6551 | 11 | 2.6684 | 13.5 | 8.4249 | 15 | 8.4413 | 15.3 | 11.6406 | 17 | 11.658 | 18.9 | 16.6466 | 21 | 16.6601 | 22.5 | 28.4628 | 25 | 28.4768 | 28.8 | 37.3239 | 32 | 37.3372 | 35.1 | 51.7049 | 39 | 51.7184 | 43.2 | 67.2887 | 48 | 67.3018
9 | 0.9882 | 10 | 1.0018 | 10.8 | 2.065 | 12 | 2.0788 | 14.4 | 6.6851 | 16 | 6.6997 | 16.2 | 9.2498 | 18 | 9.2663 | 19.8 | 13.4183 | 22 | 13.433 | 23.4 | 22.5006 | 26 | 22.5163 | 29.7 | 29.5163 | 33 | 29.533 | 36 | 41.2064 | 40 | 41.2205 | 44.1 | 53.7658 | 49 | 53.783
9.9 | 0.7893 | 11 | 0.8038 | 11.7 | 1.6639 | 13 | 1.6768 | 15.3 | 5.481 | 17 | 5.4955 | 17.1 | 7.6006 | 19 | 7.6163 | 20.7 | 11.1549 | 23 | 11.1684 | 24.3 | 18.4789 | 27 | 18.4934 | 30.6 | 24.2808 | 34 | 24.2934 | 36.9 | 34.107 | 41 | 34.1205 | 45 | 44.6165 | 50 | 44.633
10.8 | 0.6475 | 12 | 0.6622 | 12.6 | 1.376 | 14 | 1.3913 | 16.2 | 4.6024 | 18 | 4.6163 | 18 | 6.3987 | 20 | 6.4122 | 21.6 | 9.4847 | 24 | 9.4997 | 25.2 | 15.5882 | 28 | 15.6018 | 31.5 | 20.5312 | 35 | 20.5455 | 37.8 | 28.9892 | 42 | 29.0018 | 45.9 | 38.0166 | 51 | 38.033
11.7 | 0.5421 | 13 | 0.558 | 13.5 | 1.1607 | 15 | 1.1747 | 17.1 | 3.9362 | 19 | 3.9497 | 18.9 | 5.4868 | 21 | 5.5018 | 22.5 | 8.2043 | 25 | 8.2184 | 26.1 | 13.414 | 29 | 13.4268 | 32.4 | 17.7168 | 36 | 17.733 | 38.7 | 25.1284 | 43 | 25.1434 | 46.8 | 33.0334 | 52 | 33.0497
12.6 | 0.4615 | 14 | 0.4768 | 14.4 | 0.99489 | 16 | 1.0101 | 18 | 3.4154 | 20 | 3.4288 | 19.8 | 4.7739 | 22 | 4.7872 | 23.4 | 7.1939 | 26 | 7.208 | 27 | 11.722 | 30 | 11.7351 | 33.3 | 15.5283 | 37 | 15.5434 | 39.6 | 22.1146 | 44 | 22.1288 | 47.7 | 29.1397 | 53 | 29.1538
13.5 | 0.3983 | 15 | 0.4122 | 15.3 | 0.8637 | 17 | 0.87675 | 18.9 | 2.9985 | 21 | 3.0122 | 20.7 | 4.2026 | 23 | 4.2163 | 24.3 | 6.378 | 27 | 6.3913 | 27.9 | 10.37 | 31 | 10.3851 | 34.2 | 13.7799 | 38 | 13.7934 | 40.5 | 19.6978 | 45 | 19.7122 | 48.6 | 26.0156 | 54 | 26.033
14.4 | 0.3478 | 16 | 0.3622 | 16.2 | 0.75817 | 18 | 0.77467 | 19.8 | 2.6585 | 22 | 2.6747 | 21.6 | 3.7361 | 24 | 3.7497 | 25.2 | 5.7066 | 28 | 5.7205 | 28.8 | 9.2664 | 32 | 9.283 | 35.1 | 12.3523 | 39 | 12.3663 | 41.4 | 17.7184 | 46 | 17.733 | 49.5 | 23.4546 | 55 | 23.4684
15.3 | 0.3066 | 17 | 0.3205 | 17.1 | 0.67175 | 19 | 0.68509 | 20.7 | 2.3767 | 23 | 2.3913 | 22.5 | 3.3487 | 25 | 3.3622 | 26.1 | 5.1454 | 29 | 5.1601 | 29.7 | 8.3499 | 33 | 8.3663 | 36 | 11.1656 | 40 | 11.183 | 42.3 | 16.0682 | 47 | 16.083 | 50.4 | 21.3173 | 56 | 21.333
16.2 | 0.2727 | 18 | 0.2872 | 18 | 0.59992 | 20 | 0.61634 | 21.6 | 2.14 | 24 | 2.1538 | 23.4 | 3.0227 | 26 | 3.0372 | 27 | 4.6702 | 30 | 4.6851 | 30.6 | 7.5774 | 34 | 7.5913 | 36.9 | 10.1645 | 41 | 10.1788 | 43.2 | 14.6726 | 48 | 14.6872 | 51.3 | 19.508 | 57 | 19.5247
17.1 | 0.2445 | 19 | 0.258 | 18.9 | 0.53934 | 21 | 0.55384 | 22.5 | 1.9388 | 25 | 1.9518 | 24.3 | 2.7452 | 27 | 2.7601 | 27.9 | 4.2634 | 31 | 4.2768 | 31.5 | 6.9186 | 35 | 6.933 | 37.8 | 9.3095 | 42 | 9.3247 | 44.1 | 13.4774 | 49 | 13.4913 | 52.2 | 17.9571 | 58 | 17.9747
18 | 0.2206 | 20 | 0.2351 | 19.8 | 0.48796 | 22 | 0.50175 | 23.4 | 1.7662 | 26 | 1.783 | 25.2 | 2.5065 | 28 | 2.5205 | 28.8 | 3.9116 | 32 | 3.9268 | 32.4 | 6.3506 | 36 | 6.3663 | 38.7 | 8.5712 | 43 | 8.5851 | 45 | 12.4431 | 50 | 12.458 | 53.1 | 16.6134 | 59 | 16.6268
18.9 | 0.2001 | 21 | 0.2163 | 20.7 | 0.44375 | 23 | 0.458 | 24.3 | 1.6168 | 27 | 1.633 | 26.1 | 2.2994 | 29 | 2.3163 | 29.7 | 3.6048 | 33 | 3.6184 | 33.3 | 5.8563 | 37 | 5.8705 | 39.6 | 7.9279 | 44 | 7.9413 | 45.9 | 11.5398 | 51 | 11.5538 | 54 | 15.4384 | 60 | 15.4518
19.8 | 0.1825 | 22 | 0.1997 | 21.6 | 0.40571 | 24 | 0.41842 | 25.2 | 1.4864 | 28 | 1.4997 | 27 | 2.1183 | 30 | 2.133 | 30.6 | 3.3352 | 34 | 3.3497 | 34.2 | 5.4229 | 38 | 5.4372 | 40.5 | 7.3627 | 45 | 7.3768 | 46.8 | 10.7444 | 52 | 10.758 | 54.9 | 14.4029 | 61 | 14.4184
20.7 | 0.167 | 23 | 0.183 | 22.5 | 0.37242 | 25 | 0.38509 | 26.1 | 1.3718 | 29 | 1.3851 | 27.9 | 1.959 | 31 | 1.9747 | 31.5 | 3.0969 | 35 | 3.1101 | 35.1 | 5.04 | 39 | 5.0538 | 41.4 | 6.8626 | 46 | 6.8768 | 47.7 | 10.0391 | 53 | 10.0538 | 55.8 | 13.4837 | 62 | 13.4997
21.6 | 0.1538 | 24 | 0.1684 | 23.4 | 0.34331 | 26 | 0.358 | 27 | 1.2705 | 30 | 1.2851 | 28.8 | 1.8178 | 32 | 1.833 | 32.4 | 2.8849 | 36 | 2.8997 | 36 | 4.6996 | 40 | 4.7163 | 42.3 | 6.4172 | 47 | 6.433 | 48.6 | 9.4098 | 54 | 9.4247 | 56.7 | 12.6623 | 63 | 12.6768
22.5 | 0.142 | 25 | 0.158 | 24.3 | 0.31761 | 27 | 0.333 | 27.9 | 1.1806 | 31 | 1.1934 | 29.7 | 1.6922 | 33 | 1.708 | 33.3 | 2.6952 | 37 | 2.7101 | 36.9 | 4.3954 | 41 | 4.4101 | 43.2 | 6.0182 | 48 | 6.033 | 49.5 | 8.8451 | 55 | 8.8601 | 57.6 | 11.9245 | 64 | 11.9413
23.4 | 0.1319 | 26 | 0.1483 | 25.2 | 0.29478 | 28 | 0.308 | 28.8 | 1.1002 | 32 | 1.1163 | 30.6 | 1.5796 | 34 | 1.5934 | 34.2 | 2.5248 | 38 | 2.5413 | 37.8 | 4.122 | 42 | 4.1351 | 44.1 | 5.6591 | 49 | 5.6747 | 50.4 | 8.3357 | 56 | 8.3497 | 58.5 | 11.2582 | 65 | 11.2747
24.3 | 0.1227 | 27 | 0.1399 | 26.1 | 0.27445 | 29 | 0.29134 | 29.7 | 1.0281 | 33 | 1.0434 | 31.5 | 1.4786 | 35 | 1.4934 | 35.1 | 2.3709 | 39 | 2.3851 | 38.7 | 3.8753 | 43 | 3.8913 | 45 | 5.3343 | 50 | 5.3497 | 51.3 | 7.8741 | 57 | 7.8913 | 59.4 | 10.6538 | 66 | 10.6684
25.2 | 0.1145 | 28 | 0.1316 | 27 | 0.25621 | 30 | 0.2705 | 30.6 | 0.963 | 34 | 0.97675 | 32.4 | 1.3873 | 36 | 1.4018 | 36 | 2.2314 | 40 | 2.2455 | 39.6 | 3.6516 | 44 | 3.6663 | 45.9 | 5.0393 | 51 | 5.0538 | 52.2 | 7.454 | 58 | 7.4684 | 60.3 | 10.1031 | 67 | 10.1184
26.1 | 0.1072 | 29 | 0.1247 | 27.9 | 0.23989 | 31 | 0.25384 | 31.5 | 0.90428 | 35 | 0.91842 | 33.3 | 1.3045 | 37 | 1.3184 | 36.9 | 2.1046 | 41 | 2.1184 | 40.5 | 3.4481 | 45 | 3.4622 | 46.8 | 4.7703 | 52 | 4.7851 | 53.1 | 7.0704 | 59 | 7.0851 | 61.2 | 9.5995 | 68 | 9.6163
27 | 0.1007 | 30 | 0.1163 | 28.8 | 0.22511 | 32 | 0.24134 | 32.4 | 0.8509 | 36 | 0.86634 | 34.2 | 1.2293 | 38 | 1.2434 | 37.8 | 1.9888 | 42 | 2.0018 | 41.4 | 3.2622 | 46 | 3.2768 | 47.7 | 4.5242 | 53 | 4.5413 | 54 | 6.7188 | 60 | 6.733 | 62.1 | 9.1374 | 69 | 9.1518
27.9 | 0.0948 | 31 | 0.1101 | 29.7 | 0.21172 | 33 | 0.22675 | 33.3 | 0.80229 | 37 | 0.81634 | 35.1 | 1.1606 | 39 | 1.1747 | 38.7 | 1.8828 | 43 | 1.8997 | 42.3 | 3.092 | 47 | 3.108 | 48.6 | 4.2983 | 54 | 4.3122 | 54.9 | 6.3954 | 61 | 6.4101 | 63 | 8.7119 | 70 | 8.7268
28.8 | 0.0894 | 32 | 0.1066 | 30.6 | 0.1995 | 34 | 0.21634 | 34.2 | 0.75786 | 38 | 0.77467 | 36 | 1.0977 | 40 | 1.1122 | 39.6 | 1.7853 | 44 | 1.7997 | 43.2 | 2.9355 | 48 | 2.9497 | 49.5 | 4.0903 | 55 | 4.1038 | 55.8 | 6.0971 | 62 | 6.1101 | 63.9 | 8.3191 | 71 | 8.333
29.7 | 0.0845 | 33 | 0.0997 | 31.5 | 0.18849 | 35 | 0.20175 | 35.1 | 0.71716 | 39 | 0.733 | 36.9 | 1.04 | 41 | 1.0538 | 40.5 | 1.6957 | 45 | 1.7101 | 44.1 | 2.7913 | 49 | 2.808 | 50.4 | 3.8982 | 56 | 3.9122 | 56.7 | 5.8213 | 63 | 5.8351 | 64.8 | 7.9553 | 72 | 7.9684
30.6 | 0.0801 | 34 | 0.0941 | 32.4 | 0.17811 | 36 | 0.19342 | 36 | 0.6797 | 40 | 0.69342 | 37.8 | 0.98685 | 42 | 1.0018 | 41.4 | 1.6129 | 46 | 1.6268 | 45 | 2.658 | 50 | 2.6747 | 51.3 | 3.7203 | 57 | 3.7351 | 57.6 | 5.5655 | 64 | 5.5788 | 65.7 | 7.6175 | 73 | 7.633
31.5 | 0.076 | 35 | 0.0913 | 33.3 | 0.16882 | 37 | 0.18439 | 36.9 | 0.64528 | 41 | 0.66009 | 38.7 | 0.93788 | 43 | 0.9518 | 42.3 | 1.5364 | 47 | 1.5497 | 45.9 | 2.5347 | 51 | 2.5497 | 52.2 | 3.5553 | 58 | 3.5684 | 58.5 | 5.3277 | 65 | 5.3413 | 66.6 | 7.3032 | 74 | 7.3184
32.4 | 0.0723 | 36 | 0.0899 | 34.2 | 0.16023 | 38 | 0.17606 | 37.8 | 0.6134 | 42 | 0.62675 | 39.6 | 0.89252 | 44 | 0.908 | 43.2 | 1.4653 | 48 | 1.4788 | 46.8 | 2.4202 | 52 | 2.4351 | 53.1 | 3.4019 | 59 | 3.4163 | 59.4 | 5.1063 | 66 | 5.1205 | 67.5 | 7.0101 | 75 | 7.0247
33.3 | 0.0689 | 37 | 0.0844 | 35.1 | 0.15244 | 39 | 0.16773 | 38.7 | 0.58397 | 43 | 0.59967 | 40.5 | 0.85057 | 45 | 0.8663 | 44.1 | 1.3993 | 49 | 1.4163 | 47.7 | 2.3137 | 53 | 2.3268 | 54 | 3.2588 | 60 | 3.2747 | 60.3 | 4.8995 | 67 | 4.9163 | 68.4 | 6.7361 | 76 | 6.7497
34.2 | 0.0657 | 38 | 0.083 | 36 | 0.14517 | 40 | 0.16009 | 39.6 | 0.55662 | 44 | 0.5705 | 41.4 | 0.81154 | 46 | 0.8268 | 45 | 1.3377 | 50 | 1.3518 | 48.6 | 2.2144 | 54 | 2.2288 | 54.9 | 3.1252 | 61 | 3.1413 | 61.2 | 4.7061 | 68 | 4.7205 | 69.3 | 6.4796 | 77 | 6.4934
35.1 | 0.0629 | 39 | 0.0789 | 36.9 | 0.13844 | 41 | 0.15245 | 40.5 | 0.53129 | 45 | 0.5455 | 42.3 | 0.7753 | 47 | 0.7913 | 45.9 | 1.2804 | 51 | 1.2934 | 49.5 | 2.1217 | 55 | 2.1351 | 55.8 | 3.0003 | 62 | 3.0163 | 62.1 | 4.5249 | 69 | 4.5413 | 70.2 | 6.2388 | 78 | 6.2518
36 | 0.0602 | 40 | 0.0775 | 37.8 | 0.13222 | 42 | 0.14967 | 41.4 | 0.50764 | 46 | 0.52467 | 43.2 | 0.74141 | 48 | 0.758 | 46.8 | 1.2267 | 52 | 1.2413 | 50.4 | 2.035 | 56 | 2.0497 | 56.7 | 2.8831 | 63 | 2.8997 | 63 | 4.3548 | 70 | 4.3684 | 71.1 | 6.0126 | 79 | 6.0268
36.9 | 0.0577 | 41 | 0.0761 | 38.7 | 0.12646 | 43 | 0.14273 | 42.3 | 0.48566 | 47 | 0.49967 | 44.1 | 0.70983 | 49 | 0.7247 | 47.7 | 1.1766 | 53 | 1.1913 | 51.3 | 1.9537 | 57 | 1.9684 | 57.6 | 2.7731 | 64 | 2.7872 | 63.9 | 4.1949 | 71 | 4.2101 | 72 | 5.7997 | 80 | 5.8163
37.8 | 0.0554 | 42 | 0.0732 | 39.6 | 0.12105 | 44 | 0.13578 | 43.2 | 0.46503 | 48 | 0.47884 | 45 | 0.68025 | 50 | 0.6934 | 48.6 | 1.1295 | 54 | 1.1434 | 52.2 | 1.8775 | 58 | 1.8913 | 58.5 | 2.6696 | 65 | 2.683 | 64.8 | 4.0443 | 72 | 4.058 | 72.9 | 5.5989 | 81 | 5.6122
38.7 | 0.0533 | 43 | 0.0725 | 40.5 | 0.11607 | 45 | 0.133 | 44.1 | 0.44578 | 49 | 0.46009 | 45.9 | 0.65257 | 51 | 0.6663 | 49.5 | 1.0854 | 55 | 1.0997 | 53.1 | 1.8058 | 59 | 1.8184 | 59.4 | 2.5722 | 66 | 2.5851 | 65.7 | 3.9022 | 73 | 3.9163 | 73.8 | 5.4094 | 82 | 5.4247
39.6 | 0.0513 | 44 | 0.0704 | 41.4 | 0.11133 | 46 | 0.12676 | 45 | 0.42771 | 50 | 0.44134 | 46.8 | 0.62657 | 52 | 0.6413 | 50.4 | 1.0438 | 56 | 1.058 | 54 | 1.7383 | 60 | 1.7518 | 60.3 | 2.4804 | 67 | 2.4934 | 66.6 | 3.7681 | 74 | 3.783 | 74.7 | 5.2301 | 83 | 5.2434
40.5 | 0.0494 | 45 | 0.069 | 42.3 | 0.10699 | 47 | 0.12467 | 45.9 | 0.41078 | 51 | 0.42467 | 47.7 | 0.60219 | 53 | 0.6163 | 51.3 | 1.0046 | 57 | 1.0184 | 54.9 | 1.6747 | 61 | 1.6913 | 61.2 | 2.3936 | 68 | 2.408 | 67.5 | 3.6412 | 75 | 3.658 | 75.6 | 5.0605 | 84 | 5.0747
41.4 | 0.0476 | 46 | 0.069 | 43.2 | 0.10284 | 48 | 0.11841 | 46.8 | 0.39484 | 52 | 0.41009 | 48.6 | 0.57925 | 54 | 0.5934 | 52.2 | 0.96775 | 58 | 0.983 | 55.8 | 1.6146 | 62 | 1.6288 | 62.1 | 2.3116 | 69 | 2.3268 | 68.4 | 3.5211 | 76 | 3.5351 | 76.5 | 4.8997 | 85 | 4.9163
42.3 | 0.046 | 47 | 0.0677 | 44.1 | 0.099008 | 49 | 0.11634 | 47.7 | 0.37989 | 53 | 0.39342 | 49.5 | 0.55763 | 55 | 0.5747 | 53.1 | 0.93291 | 59 | 0.94967 | 56.7 | 1.5579 | 63 | 1.5747 | 63 | 2.234 | 70 | 2.2497 | 69.3 | 3.4072 | 77 | 3.4205 | 77.4 | 4.747 | 86 | 4.7601
43.2 | 0.0445 | 48 | 0.0664 | 45 | 0.095372 | 50 | 0.1101 | 48.6 | 0.3658 | 54 | 0.383 | 50.4 | 0.53723 | 56 | 0.5518 | 54 | 0.9 | 60 | 0.91634 | 57.6 | 1.5042 | 64 | 1.5184 | 63.9 | 2.1604 | 71 | 2.1747 | 70.2 | 3.2992 | 78 | 3.3163 | 78.3 | 4.602 | 87 | 4.6163
44.1 | 0.043 | 49 | 0.065 | 45.9 | 0.091997 | 51 | 0.108 | 49.5 | 0.35251 | 55 | 0.36634 | 51.3 | 0.51794 | 57 | 0.533 | 54.9 | 0.86885 | 61 | 0.883 | 58.5 | 1.4533 | 65 | 1.4684 | 64.8 | 2.0906 | 72 | 2.1038 | 71.1 | 3.1965 | 79 | 3.2101 | 79.2 | 4.4641 | 88 | 4.4768
95.4 | 0.0359 | 50 | 0.065 | 46.8 | 0.088771 | 52 | 0.10591 | 50.4 | 0.33995 | 56 | 0.35384 | 52.2 | 0.49973 | 58 | 0.5163 | 55.8 | 0.83933 | 62 | 0.85384 | 59.4 | 1.4052 | 66 | 1.4184 | 65.7 | 2.0243 | 73 | 2.0413 | 72 | 3.0988 | 80 | 3.1122 | 80.1 | 4.3328 | 89 | 4.3497
250.2 | 0.034 | 51 | 0.0637 | 47.7 | 0.085753 | 53 | 0.10105 | 51.3 | 0.32805 | 57 | 0.34134 | 53.1 | 0.48249 | 59 | 0.4997 | 56.7 | 0.81134 | 63 | 0.82467 | 60.3 | 1.3594 | 67 | 1.3747 | 66.6 | 1.9613 | 74 | 1.9747 | 72.9 | 3.0059 | 81 | 3.0184 | 81 | 4.2076 | 90 | 4.2247
250.2 | 0.0073 | 52 | 0.0623 | 48.6 | 0.082925 | 54 | 0.099673 | 52.2 | 0.3168 | 58 | 0.333 | 54 | 0.46617 | 60 | 0.483 | 57.6 | 0.78477 | 64 | 0.79967 | 61.2 | 1.3159 | 68 | 1.333 | 67.5 | 1.9013 | 75 | 1.9163 | 73.8 | 2.9173 | 82 | 2.933 | 81.9 | 4.0882 | 91 | 4.1018
468 | 0.003 | 53 | 0.0623 | 49.5 | 0.080179 | 55 | 0.09414 | 53.1 | 0.30615 | 59 | 0.3205 | 54.9 | 0.45067 | 61 | 0.4663 | 58.5 | 0.75951 | 65 | 0.77467 | 62.1 | 1.2746 | 69 | 1.2913 | 68.4 | 1.8441 | 76 | 1.858 | 74.7 | 2.8328 | 83 | 2.8497 | 82.8 | 3.9742 | 92 | 3.9913
6300 | 0.003 | 54 | 0.0609 | 50.4 | 0.077641 | 56 | 0.092739 | 54 | 0.29605 | 60 | 0.31009 | 55.8 | 0.43597 | 62 | 0.4497 | 59.4 | 0.73553 | 66 | 0.74967 | 63 | 1.2352 | 70 | 1.2497 | 69.3 | 1.7896 | 77 | 1.8038 | 75.6 | 2.7521 | 84 | 2.7663 | 83.7 | 3.8653 | 93 | 3.8788
|  | 55 | 0.0602 | 51.3 | 0.075222 | 57 | 0.091333 | 54.9 | 0.28645 | 61 | 0.30175 | 56.7 | 0.42199 | 63 | 0.4351 | 60.3 | 0.71265 | 67 | 0.72675 | 63.9 | 1.1977 | 71 | 1.2122 | 70.2 | 1.7376 | 78 | 1.7518 | 76.5 | 2.6751 | 85 | 2.6913 | 84.6 | 3.761 | 94 | 3.7747
|  | 56 | 0.0595 | 52.2 | 0.072941 | 58 | 0.089925 | 55.8 | 0.27734 | 62 | 0.29134 | 57.6 | 0.40869 | 64 | 0.4247 | 61.2 | 0.69088 | 68 | 0.708 | 64.8 | 1.1619 | 72 | 1.1768 | 71.1 | 1.6879 | 79 | 1.7018 | 77.4 | 2.6014 | 86 | 2.6163 | 85.5 | 3.6613 | 95 | 3.6747
|  | 57 | 0.058 | 53.1 | 0.070777 | 59 | 0.085744 | 56.7 | 0.26867 | 63 | 0.283 | 58.5 | 0.39602 | 65 | 0.4101 | 62.1 | 0.67014 | 69 | 0.68509 | 65.7 | 1.1278 | 73 | 1.1413 | 72 | 1.6405 | 80 | 1.6538 | 78.3 | 2.5308 | 87 | 2.5455 | 86.4 | 3.5657 | 96 | 3.5788
|  | 58 | 0.058 | 54 | 0.06873 | 60 | 0.084373 | 57.6 | 0.26041 | 64 | 0.27467 | 59.4 | 0.38399 | 66 | 0.3997 | 63 | 0.65031 | 70 | 0.66634 | 66.6 | 1.0952 | 74 | 1.1101 | 72.9 | 1.595 | 81 | 1.6101 | 79.2 | 2.4633 | 88 | 2.4768 | 87.3 | 3.4741 | 97 | 3.4872
|  | 59 | 0.058 | 54.9 | 0.066742 | 61 | 0.08301 | 58.5 | 0.25253 | 65 | 0.26634 | 60.3 | 0.37247 | 67 | 0.3872 | 63.9 | 0.63143 | 71 | 0.6455 | 67.5 | 1.0641 | 75 | 1.0768 | 73.8 | 1.5516 | 82 | 1.5663 | 80.1 | 2.3986 | 89 | 2.4122 | 88.2 | 3.3862 | 98 | 3.3997
|  | 60 | 0.058 | 55.8 | 0.064898 | 62 | 0.081649 | 59.4 | 0.24505 | 66 | 0.26009 | 61.2 | 0.3615 | 68 | 0.3768 | 64.8 | 0.61334 | 72 | 0.62675 | 68.4 | 1.0343 | 76 | 1.0497 | 74.7 | 1.5099 | 83 | 1.5247 | 81 | 2.3365 | 90 | 2.3518 | 89.1 | 3.3018 | 99 | 3.3163
|  | 61 | 0.0565 | 56.7 | 0.063082 | 63 | 0.077503 | 60.3 | 0.23787 | 67 | 0.25175 | 62.1 | 0.35103 | 69 | 0.3663 | 65.7 | 0.59606 | 73 | 0.61009 | 69.3 | 1.0057 | 77 | 1.0184 | 75.6 | 1.47 | 84 | 1.4851 | 81.9 | 2.277 | 91 | 2.2913 | 90 | 3.2207 | 100 | 3.2351
|  | 500 | 0.048 | 57.6 | 0.061405 | 64 | 0.076797 | 61.2 | 0.23104 | 68 | 0.2455 | 63 | 0.34102 | 70 | 0.358 | 66.6 | 0.57953 | 74 | 0.59342 | 70.2 | 0.9784 | 78 | 0.99342 | 76.5 | 1.4317 | 85 | 1.4455 | 82.8 | 2.2197 | 92 | 2.2351 | 90.9 | 3.1428 | 101 | 3.158
|  | 500 | 0.033 | 58.5 | 0.059804 | 65 | 0.076088 | 62.1 | 0.22453 | 69 | 0.24134 | 63.9 | 0.33147 | 71 | 0.3455 | 67.5 | 0.56371 | 75 | 0.57675 | 71.1 | 0.95222 | 79 | 0.96634 | 77.4 | 1.395 | 86 | 1.4101 | 83.7 | 2.1648 | 93 | 2.1788 | 91.8 | 3.0678 | 102 | 3.083
|  | 1000 | 0.033 | 59.4 | 0.058267 | 66 | 0.074661 | 63 | 0.21828 | 70 | 0.233 | 64.8 | 0.3223 | 72 | 0.3351 | 68.4 | 0.54853 | 76 | 0.56217 | 72 | 0.92709 | 80 | 0.94134 | 78.3 | 1.3597 | 87 | 1.3747 | 84.6 | 2.1119 | 94 | 2.1268 | 92.7 | 2.9957 | 103 | 3.0101
|  | 6300 | 0.022 | 60.3 | 0.056811 | 67 | 0.073231 | 63.9 | 0.21233 | 71 | 0.22675 | 65.7 | 0.31354 | 73 | 0.3268 | 69.3 | 0.53397 | 77 | 0.54967 | 72.9 | 0.90297 | 81 | 0.91634 | 79.2 | 1.3258 | 88 | 1.3413 | 85.5 | 2.0611 | 95 | 2.0747 | 93.6 | 2.9262 | 104 | 2.9413
|  |  |  | 61.2 | 0.055428 | 68 | 0.069033 | 64.8 | 0.2066 | 72 | 0.2205 | 66.6 | 0.30516 | 74 | 0.3184 | 70.2 | 0.51999 | 78 | 0.53509 | 73.8 | 0.87981 | 82 | 0.89342 | 80.1 | 1.2931 | 89 | 1.308 | 86.4 | 2.0121 | 96 | 2.0268 | 94.5 | 2.8593 | 105 | 2.8747
|  |  |  | 62.1 | 0.054063 | 69 | 0.068355 | 65.7 | 0.20114 | 73 | 0.21634 | 67.5 | 0.29711 | 75 | 0.3101 | 71.1 | 0.50659 | 79 | 0.5205 | 74.7 | 0.85759 | 83 | 0.87467 | 81 | 1.2617 | 90 | 1.2768 | 87.3 | 1.965 | 97 | 1.9788 | 95.4 | 2.7947 | 106 | 2.8101
|  |  |  | 63 | 0.052744 | 70 | 0.067683 | 66.6 | 0.1959 | 74 | 0.21009 | 68.4 | 0.28939 | 76 | 0.3038 | 72 | 0.49371 | 80 | 0.508 | 75.6 | 0.8362 | 84 | 0.84967 | 81.9 | 1.2316 | 91 | 1.2455 | 88.2 | 1.9195 | 98 | 1.933 | 96.3 | 2.7325 | 107 | 2.7497
|  |  |  | 63.9 | 0.051559 | 71 | 0.067683 | 67.5 | 0.19055 | 75 | 0.208 | 69.3 | 0.28197 | 77 | 0.2955 | 72.9 | 0.48131 | 81 | 0.4955 | 76.5 | 0.81564 | 85 | 0.833 | 82.8 | 1.2025 | 92 | 1.2163 | 89.1 | 1.8757 | 99 | 1.8913 | 97.2 | 2.6724 | 108 | 2.6851
|  |  |  | 64.8 | 0.050355 | 72 | 0.066351 | 68.4 | 0.18571 | 76 | 0.20106 | 70.2 | 0.27483 | 78 | 0.2913 | 73.8 | 0.46941 | 82 | 0.483 | 77.4 | 0.79583 | 86 | 0.81009 | 83.7 | 1.1744 | 93 | 1.1913 | 90 | 1.8335 | 100 | 1.8497 | 98.1 | 2.6144 | 109 | 2.6288
|  |  |  | 65.7 | 0.049222 | 73 | 0.066351 | 69.3 | 0.18107 | 77 | 0.19828 | 71.1 | 0.268 | 79 | 0.283 | 74.7 | 0.45797 | 83 | 0.47467 | 78.3 | 0.77674 | 87 | 0.79134 | 84.6 | 1.1474 | 94 | 1.1601 | 90.9 | 1.7927 | 101 | 1.808 | 99 | 2.5584 | 110 | 2.5747
|  |  |  | 66.6 | 0.048125 | 74 | 0.065023 | 70.2 | 0.17663 | 78 | 0.19273 | 72 | 0.26141 | 80 | 0.2747 | 75.6 | 0.44694 | 84 | 0.46009 | 79.2 | 0.75839 | 88 | 0.77467 | 85.5 | 1.1213 | 95 | 1.1351 | 91.8 | 1.7533 | 102 | 1.7684 | 99.9 | 2.5042 | 111 | 2.5184
|  |  |  | 67.5 | 0.04709 | 75 | 0.065023 | 71.1 | 0.17233 | 79 | 0.18995 | 72.9 | 0.25506 | 81 | 0.2684 | 76.5 | 0.43633 | 85 | 0.44967 | 80.1 | 0.74069 | 89 | 0.758 | 86.4 | 1.0961 | 96 | 1.1101 | 92.7 | 1.7152 | 103 | 1.7288 | 100.8 | 2.4519 | 112 | 2.4663
|  |  |  | 68.4 | 0.04608 | 76 | 0.060901 | 72 | 0.16822 | 80 | 0.18439 | 73.8 | 0.24896 | 82 | 0.2663 | 77.4 | 0.42608 | 86 | 0.44134 | 81 | 0.72361 | 90 | 0.73717 | 87.3 | 1.0718 | 97 | 1.0851 | 93.6 | 1.6785 | 104 | 1.6934 | 101.7 | 2.4013 | 113 | 2.4163
|  |  |  | 69.3 | 0.045116 | 77 | 0.060182 | 72.9 | 0.16424 | 81 | 0.18161 | 74.7 | 0.24312 | 83 | 0.258 | 78.3 | 0.4162 | 87 | 0.433 | 81.9 | 0.70718 | 91 | 0.7205 | 88.2 | 1.0484 | 98 | 1.0622 | 94.5 | 1.6429 | 105 | 1.658 | 102.6 | 2.3523 | 114 | 2.3663
|  |  |  | 70.2 | 0.044214 | 78 | 0.059455 | 73.8 | 0.16042 | 82 | 0.17606 | 75.6 | 0.23746 | 84 | 0.2518 | 79.2 | 0.4067 | 88 | 0.4205 | 82.8 | 0.69126 | 92 | 0.708 | 89.1 | 1.0257 | 99 | 1.0413 | 95.4 | 1.6086 | 106 | 1.6247 | 103.5 | 2.3048 | 115 | 2.3184
|  |  |  | 140.4 | 0.036262 | 79 | 0.059455 | 74.7 | 0.15673 | 83 | 0.17328 | 76.5 | 0.23201 | 85 | 0.2455 | 80.1 | 0.39752 | 89 | 0.41217 | 83.7 | 0.67592 | 93 | 0.69134 | 90 | 1.0037 | 100 | 1.0184 | 96.3 | 1.5753 | 107 | 1.5913 | 104.4 | 2.2588 | 116 | 2.2747
|  |  |  | 250.2 | 0.034627 | 80 | 0.057982 | 75.6 | 0.15318 | 84 | 0.16842 | 77.4 | 0.22674 | 86 | 0.2413 | 81 | 0.38865 | 90 | 0.40175 | 84.6 | 0.6611 | 94 | 0.67467 | 90.9 | 0.98252 | 101 | 0.99967 | 97.2 | 1.5431 | 108 | 1.558 | 105.3 | 2.2143 | 117 | 2.2288
|  |  |  | 250.2 | 0.0072687 | 500 | 0.048 | 76.5 | 0.14978 | 85 | 0.16634 | 78.3 | 0.22165 | 87 | 0.2351 | 81.9 | 0.38012 | 91 | 0.39342 | 85.5 | 0.64675 | 95 | 0.66009 | 91.8 | 0.96198 | 102 | 0.97675 | 98.1 | 1.5119 | 109 | 1.5268 | 106.2 | 2.1711 | 118 | 2.1851
|  |  |  | 468 | 0.003 | 500 | 0.033 | 77.4 | 0.14647 | 86 | 0.16078 | 79.2 | 0.21678 | 88 | 0.233 | 82.8 | 0.37184 | 92 | 0.38509 | 86.4 | 0.63288 | 96 | 0.64967 | 92.7 | 0.9421 | 103 | 0.958 | 99 | 1.4817 | 110 | 1.4955 | 107.1 | 2.1293 | 119 | 2.1434
|  |  |  | 6300 | 0.003 | 1000 | 0.033 | 78.3 | 0.14326 | 87 | 0.15939 | 80.1 | 0.21204 | 89 | 0.2268 | 83.7 | 0.36384 | 93 | 0.37675 | 87.3 | 0.61948 | 97 | 0.633 | 93.6 | 0.92288 | 104 | 0.93717 | 99.9 | 1.4524 | 111 | 1.4663 | 108 | 2.0887 | 120 | 2.1018
[6 empty] | 6300 | 0.022 | 79.2 | 0.14022 | 88 | 0.15661 | 81 | 0.20747 | 90 | 0.2247 | 84.6 | 0.35613 | 94 | 0.3705 | 88.2 | 0.6065 | 98 | 0.6205 | 94.5 | 0.90425 | 105 | 0.91842 | 100.8 | 1.424 | 112 | 1.4413 | 108.9 | 2.0493 | 121 | 2.0663
[8 empty] | 80.1 | 0.13728 | 89 | 0.15175 | 81.9 | 0.20311 | 91 | 0.2163 | 85.5 | 0.34864 | 95 | 0.36217 | 89.1 | 0.59396 | 99 | 0.608 | 95.4 | 0.8862 | 106 | 0.89967 | 101.7 | 1.3965 | 113 | 1.4101 | 109.8 | 2.0111 | 122 | 2.0247
[8 empty] | 81 | 0.13439 | 90 | 0.14967 | 82.8 | 0.19883 | 92 | 0.2122 | 86.4 | 0.34139 | 96 | 0.358 | 90 | 0.58179 | 100 | 0.5955 | 96.3 | 0.86871 | 107 | 0.883 | 102.6 | 1.3698 | 114 | 1.3851 | 110.7 | 1.974 | 123 | 1.9913
[8 empty] | 81.9 | 0.13162 | 91 | 0.14828 | 83.7 | 0.1947 | 93 | 0.208 | 87.3 | 0.33439 | 97 | 0.34967 | 90.9 | 0.57001 | 101 | 0.58509 | 97.2 | 0.85173 | 108 | 0.86634 | 103.5 | 1.3438 | 115 | 1.358 | 111.6 | 1.9379 | 124 | 1.9518
[8 empty] | 82.8 | 0.12893 | 92 | 0.14342 | 84.6 | 0.19041 | 94 | 0.208 | 88.2 | 0.32761 | 98 | 0.34134 | 91.8 | 0.55856 | 102 | 0.57467 | 98.1 | 0.83527 | 109 | 0.84967 | 104.4 | 1.3187 | 116 | 1.333 | 112.5 | 1.9029 | 125 | 1.9163
[8 empty] | 83.7 | 0.12634 | 93 | 0.14134 | 85.5 | 0.18656 | 95 | 0.2018 | 89.1 | 0.32103 | 99 | 0.33509 | 92.7 | 0.5475 | 103 | 0.56217 | 99 | 0.8193 | 110 | 0.833 | 105.3 | 1.2942 | 117 | 1.308 | 113.4 | 1.8688 | 126 | 1.883
[8 empty] | 84.6 | 0.12383 | 94 | 0.14134 | 86.4 | 0.18281 | 96 | 0.1997 | 90 | 0.31466 | 100 | 0.32884 | 93.6 | 0.53679 | 104 | 0.55175 | 99.9 | 0.80378 | 111 | 0.81842 | 106.2 | 1.2705 | 118 | 1.2851 | 114.3 | 1.8357 | 127 | 1.8497
[8 empty] | 85.5 | 0.1214 | 95 | 0.13578 | 87.3 | 0.17918 | 97 | 0.1941 | 90.9 | 0.30848 | 101 | 0.32467 | 94.5 | 0.52638 | 105 | 0.54134 | 100.8 | 0.78874 | 112 | 0.80175 | 107.1 | 1.2474 | 119 | 1.2601 | 115.2 | 1.8035 | 128 | 1.8184
[8 empty] | 86.4 | 0.11905 | 96 | 0.13439 | 88.2 | 0.17568 | 98 | 0.1913 | 91.8 | 0.30247 | 102 | 0.31634 | 95.4 | 0.51629 | 106 | 0.533 | 101.7 | 0.77412 | 113 | 0.79134 | 108 | 1.2249 | 120 | 1.2413 | 116.1 | 1.7722 | 129 | 1.7851
[8 empty] | 87.3 | 0.11675 | 97 | 0.133 | 89.1 | 0.17227 | 99 | 0.1899 | 92.7 | 0.29665 | 103 | 0.31009 | 96.3 | 0.50649 | 107 | 0.5205 | 102.6 | 0.75991 | 114 | 0.77467 | 108.9 | 1.2031 | 121 | 1.2184 | 117 | 1.7418 | 130 | 1.758
[8 empty] | 88.2 | 0.11456 | 98 | 0.13162 | 90 | 0.16897 | 100 | 0.1844 | 93.6 | 0.29103 | 104 | 0.308 | 97.2 | 0.49696 | 108 | 0.51009 | 103.5 | 0.7461 | 115 | 0.76009 | 109.8 | 1.1819 | 122 | 1.1955 | 117.9 | 1.7121 | 131 | 1.7268
[8 empty] | 89.1 | 0.11241 | 99 | 0.12745 | 90.9 | 0.16577 | 101 | 0.183 | 94.5 | 0.28556 | 105 | 0.29967 | 98.1 | 0.48773 | 109 | 0.50175 | 104.4 | 0.73268 | 116 | 0.74967 | 110.7 | 1.1613 | 123 | 1.1747 | 118.8 | 1.6832 | 132 | 1.6997
[8 empty] | 90 | 0.11032 | 100 | 0.12606 | 91.8 | 0.16268 | 102 | 0.1774 | 95.4 | 0.28025 | 106 | 0.29342 | 99 | 0.47875 | 110 | 0.49342 | 105.3 | 0.71962 | 117 | 0.733 | 111.6 | 1.1412 | 124 | 1.158 | 119.7 | 1.6551 | 133 | 1.6684
[8 empty] | 90.9 | 0.10832 | 101 | 0.12467 | 92.7 | 0.15966 | 103 | 0.1747 | 96.3 | 0.2751 | 107 | 0.29134 | 99.9 | 0.47002 | 111 | 0.48509 | 106.2 | 0.70692 | 118 | 0.7205 | 112.5 | 1.1216 | 125 | 1.1351 | 120.6 | 1.6277 | 134 | 1.6413
[8 empty] | 91.8 | 0.10636 | 102 | 0.12328 | 93.6 | 0.15673 | 104 | 0.1733 | 97.2 | 0.27008 | 108 | 0.28509 | 100.8 | 0.46155 | 112 | 0.47675 | 107.1 | 0.69457 | 119 | 0.708 | 113.4 | 1.1026 | 126 | 1.1163 | 121.5 | 1.601 | 135 | 1.6163
[8 empty] | 92.7 | 0.10446 | 103 | 0.11911 | 94.5 | 0.15389 | 105 | 0.1684 | 98.1 | 0.26522 | 109 | 0.27884 | 101.7 | 0.45332 | 113 | 0.46842 | 108 | 0.68254 | 120 | 0.69967 | 114.3 | 1.0841 | 127 | 1.0997 | 122.4 | 1.575 | 136 | 1.5913
[8 empty] | 93.6 | 0.10262 | 104 | 0.11772 | 95.4 | 0.15114 | 106 | 0.1663 | 99 | 0.26049 | 110 | 0.27467 | 102.6 | 0.44529 | 114 | 0.46009 | 108.9 | 0.67083 | 121 | 0.68509 | 115.2 | 1.066 | 128 | 1.083 | 123.3 | 1.5496 | 137 | 1.5663
[8 empty] | 94.5 | 0.10081 | 105 | 0.11634 | 96.3 | 0.14846 | 107 | 0.1649 | 99.9 | 0.25588 | 111 | 0.2705 | 103.5 | 0.43747 | 115 | 0.45175 | 109.8 | 0.65943 | 122 | 0.67467 | 116.1 | 1.0484 | 129 | 1.0622 | 124.2 | 1.5249 | 138 | 1.5413
[8 empty] | 95.4 | 0.099076 | 106 | 0.11634 | 97.2 | 0.14585 | 108 | 0.1608 | 100.8 | 0.25141 | 112 | 0.26634 | 104.4 | 0.42989 | 116 | 0.44342 | 110.7 | 0.64835 | 123 | 0.66217 | 117 | 1.0313 | 130 | 1.0455 | 125.1 | 1.5008 | 139 | 1.5163
[8 empty] | 96.3 | 0.097394 | 107 | 0.11496 | 98.1 | 0.14333 | 109 | 0.1594 | 101.7 | 0.24707 | 113 | 0.26009 | 105.3 | 0.42249 | 117 | 0.43717 | 111.6 | 0.63755 | 124 | 0.65175 | 117.9 | 1.0145 | 131 | 1.0288 | 126 | 1.4772 | 140 | 1.4913
[8 empty] | 97.2 | 0.095741 | 108 | 0.11079 | 99 | 0.14085 | 110 | 0.158 | 102.6 | 0.24283 | 114 | 0.258 | 106.2 | 0.41529 | 118 | 0.42884 | 112.5 | 0.62701 | 125 | 0.64134 | 118.8 | 0.99823 | 132 | 1.0122 | 126.9 | 1.4543 | 141 | 1.4684
[8 empty] | 98.1 | 0.09416 | 109 | 0.1094 | 99.9 | 0.13848 | 111 | 0.1524 | 103.5 | 0.23869 | 115 | 0.25175 | 107.1 | 0.40828 | 119 | 0.42467 | 113.4 | 0.61674 | 126 | 0.633 | 119.7 | 0.98233 | 133 | 0.99967 | 127.8 | 1.4318 | 142 | 1.4455
[8 empty] | 99 | 0.092591 | 110 | 0.108 | 100.8 | 0.13614 | 112 | 0.1518 | 104.4 | 0.23468 | 116 | 0.24967 | 108 | 0.40146 | 120 | 0.41634 | 114.3 | 0.60672 | 127 | 0.6205 | 120.6 | 0.96681 | 134 | 0.983 | 128.7 | 1.41 | 143 | 1.4247
[8 empty] | 99.9 | 0.091094 | 111 | 0.108 | 101.7 | 0.13389 | 113 | 0.1497 | 105.3 | 0.23078 | 117 | 0.2455 | 108.9 | 0.3948 | 121 | 0.41009 | 115.2 | 0.59697 | 128 | 0.61009 | 121.5 | 0.95167 | 135 | 0.96634 | 129.6 | 1.3886 | 144 | 1.4018
[8 empty] | 100.8 | 0.089605 | 112 | 0.1066 | 102.6 | 0.13167 | 114 | 0.1483 | 106.2 | 0.22696 | 118 | 0.24134 | 109.8 | 0.38831 | 122 | 0.40175 | 116.1 | 0.58744 | 129 | 0.60175 | 122.4 | 0.9369 | 136 | 0.95175 | 130.5 | 1.3678 | 145 | 1.383
[8 empty] | 101.7 | 0.088196 | 113 | 0.10243 | 103.5 | 0.12951 | 115 | 0.1441 | 107.1 | 0.22324 | 119 | 0.23717 | 110.7 | 0.38201 | 123 | 0.3955 | 117 | 0.57817 | 130 | 0.59342 | 123.3 | 0.92248 | 137 | 0.93717 | 131.4 | 1.3474 | 146 | 1.3601
[8 empty] | 102.6 | 0.086787 | 114 | 0.10174 | 104.4 | 0.12742 | 116 | 0.1427 | 108 | 0.21963 | 120 | 0.233 | 111.6 | 0.37586 | 124 | 0.39134 | 117.9 | 0.56909 | 131 | 0.583 | 124.2 | 0.90841 | 138 | 0.92467 | 132.3 | 1.3275 | 147 | 1.3413
[8 empty] | 103.5 | 0.085431 | 115 | 0.10105 | 105.3 | 0.12539 | 117 | 0.1413 | 108.9 | 0.2161 | 121 | 0.233 | 112.5 | 0.36984 | 125 | 0.38509 | 118.8 | 0.56026 | 132 | 0.57467 | 125.1 | 0.89464 | 139 | 0.908 | 133.2 | 1.308 | 148 | 1.3247
[8 empty] | 104.4 | 0.084109 | 116 | 0.099673 | 106.2 | 0.12342 | 118 | 0.1399 | 109.8 | 0.21266 | 122 | 0.22675 | 113.4 | 0.36399 | 126 | 0.37675 | 119.7 | 0.55163 | 133 | 0.56634 | 126 | 0.8812 | 140 | 0.8955 | 134.1 | 1.289 | 149 | 1.3018
[8 empty] | 105.3 | 0.082821 | 117 | 0.099673 | 107.1 | 0.12147 | 119 | 0.1358 | 110.7 | 0.20932 | 123 | 0.22467 | 114.3 | 0.35827 | 127 | 0.37467 | 120.6 | 0.54319 | 134 | 0.558 | 126.9 | 0.8681 | 141 | 0.883 | 135 | 1.2704 | 150 | 1.2851
[8 empty] | 106.2 | 0.081586 | 118 | 0.098297 | 108 | 0.1196 | 120 | 0.1351 | 111.6 | 0.20606 | 124 | 0.2205 | 115.2 | 0.35269 | 128 | 0.36634 | 121.5 | 0.53496 | 135 | 0.54967 | 127.8 | 0.85525 | 142 | 0.86842 | 135.9 | 1.2522 | 151 | 1.2663
[8 empty] | 107.1 | 0.080354 | 119 | 0.09414 | 108.9 | 0.11774 | 121 | 0.133 | 112.5 | 0.20287 | 125 | 0.21634 | 116.1 | 0.34724 | 129 | 0.36009 | 122.4 | 0.52693 | 136 | 0.54134 | 128.7 | 0.84275 | 143 | 0.858 | 136.8 | 1.2344 | 152 | 1.2497
[8 empty] | 108 | 0.079172 | 120 | 0.09414 | 109.8 | 0.11595 | 122 | 0.133 | 113.4 | 0.19976 | 126 | 0.21634 | 117 | 0.34194 | 130 | 0.358 | 123.3 | 0.51906 | 137 | 0.533 | 129.6 | 0.83048 | 144 | 0.84342 | 137.7 | 1.2171 | 153 | 1.233
[8 empty] | 108.9 | 0.077993 | 121 | 0.09344 | 110.7 | 0.11419 | 123 | 0.1316 | 114.3 | 0.19672 | 127 | 0.21009 | 117.9 | 0.33674 | 131 | 0.35175 | 124.2 | 0.5114 | 138 | 0.52467 | 130.5 | 0.81852 | 145 | 0.833 | 138.6 | 1.2001 | 154 | 1.2163
[8 empty] | 109.8 | 0.076865 | 122 | 0.092739 | 111.6 | 0.11251 | 124 | 0.1275 | 115.2 | 0.19346 | 128 | 0.20939 | 118.8 | 0.33169 | 132 | 0.3455 | 125.1 | 0.50389 | 139 | 0.51842 | 131.4 | 0.80678 | 146 | 0.8205 | 139.5 | 1.1834 | 155 | 1.1997
[8 empty] | 110.7 | 0.07573 | 123 | 0.091332 | 112.5 | 0.11083 | 125 | 0.1261 | 116.1 | 0.19057 | 129 | 0.208 | 119.7 | 0.32674 | 133 | 0.34134 | 126 | 0.49654 | 140 | 0.51009 | 132.3 | 0.79535 | 147 | 0.81009 | 140.4 | 1.1671 | 156 | 1.183
[8 empty] | 111.6 | 0.074692 | 124 | 0.091333 | 113.4 | 0.10921 | 126 | 0.1247 | 117 | 0.18775 | 130 | 0.20245 | 120.6 | 0.32189 | 134 | 0.33509 | 126.9 | 0.4894 | 141 | 0.50384 | 133.2 | 0.78413 | 148 | 0.79967 | 141.3 | 1.1512 | 157 | 1.1663
[8 empty] | 112.5 | 0.073621 | 125 | 0.091332 | 114.3 | 0.10761 | 127 | 0.1247 | 117.9 | 0.185 | 131 | 0.20106 | 121.5 | 0.31717 | 135 | 0.333 | 127.8 | 0.48238 | 142 | 0.49967 | 134.1 | 0.77318 | 149 | 0.78717 | 142.2 | 1.1356 | 158 | 1.1497
[8 empty] | 113.4 | 0.072591 | 126 | 0.089925 | 115.2 | 0.10607 | 128 | 0.1233 | 118.8 | 0.18229 | 132 | 0.19967 | 122.4 | 0.31255 | 136 | 0.32675 | 128.7 | 0.47554 | 143 | 0.49134 | 135 | 0.76245 | 150 | 0.77675 | 143.1 | 1.1203 | 159 | 1.1351
[8 empty] | 114.3 | 0.071587 | 127 | 0.085744 | 116.1 | 0.10455 | 129 | 0.1191 | 119.7 | 0.17965 | 133 | 0.19411 | 123.3 | 0.30803 | 137 | 0.32467 | 129.6 | 0.46882 | 144 | 0.483 | 135.9 | 0.75195 | 151 | 0.76634 | 144 | 1.1053 | 160 | 1.1184
[8 empty] | 115.2 | 0.070606 | 128 | 0.085057 | 117 | 0.10309 | 130 | 0.1184 | 120.6 | 0.17709 | 134 | 0.19273 | 124.2 | 0.30363 | 138 | 0.31842 | 130.5 | 0.46228 | 145 | 0.47675 | 136.8 | 0.74168 | 152 | 0.758 | 144.9 | 1.0907 | 161 | 1.108
[8 empty] | 116.1 | 0.069648 | 129 | 0.085057 | 117.9 | 0.10165 | 131 | 0.1177 | 121.5 | 0.17457 | 135 | 0.19134 | 125.1 | 0.2993 | 139 | 0.31634 | 131.4 | 0.45583 | 146 | 0.4705 | 137.7 | 0.73161 | 153 | 0.7455 | 145.8 | 1.0763 | 162 | 1.0913
[8 empty] | 117 | 0.068722 | 130 | 0.084373 | 118.8 | 0.10023 | 132 | 0.1163 | 122.4 | 0.17213 | 136 | 0.18925 | 126 | 0.29507 | 140 | 0.31009 | 132.3 | 0.44958 | 147 | 0.46634 | 138.6 | 0.72176 | 154 | 0.73509 | 146.7 | 1.0622 | 163 | 1.0768
[8 empty] | 117.9 | 0.067817 | 131 | 0.08301 | 119.7 | 0.098853 | 133 | 0.1163 | 123.3 | 0.16971 | 137 | 0.18509 | 126.9 | 0.29096 | 141 | 0.308 | 133.2 | 0.44342 | 148 | 0.458 | 139.5 | 0.71211 | 155 | 0.72675 | 147.6 | 1.0485 | 164 | 1.0622
[8 empty] | 118.8 | 0.066916 | 132 | 0.08301 | 120.6 | 0.097515 | 134 | 0.115 | 124.2 | 0.16737 | 138 | 0.183 | 127.8 | 0.2869 | 142 | 0.30175 | 134.1 | 0.43741 | 149 | 0.45175 | 140.4 | 0.70265 | 156 | 0.71634 | 148.5 | 1.035 | 165 | 1.0497
[8 empty] | 119.7 | 0.066041 | 133 | 0.08301 | 121.5 | 0.096187 | 135 | 0.1108 | 125.1 | 0.16506 | 139 | 0.18162 | 128.7 | 0.28297 | 143 | 0.29967 | 135 | 0.43151 | 150 | 0.4455 | 141.3 | 0.69339 | 157 | 0.708 | 149.4 | 1.0217 | 166 | 1.0351
[8 empty] | 120.6 | 0.065203 | 134 | 0.081649 | 122.4 | 0.094924 | 136 | 0.1101 | 126 | 0.16279 | 140 | 0.17745 | 129.6 | 0.27909 | 144 | 0.29342 | 135.9 | 0.42575 | 151 | 0.44134 | 142.2 | 0.68434 | 158 | 0.69967 | 150.3 | 1.0087 | 167 | 1.0247
[8 empty] | 121.5 | 0.064355 | 135 | 0.081649 | 123.3 | 0.093639 | 137 | 0.1094 | 126.9 | 0.16059 | 141 | 0.17606 | 130.5 | 0.27531 | 145 | 0.29134 | 136.8 | 0.42009 | 152 | 0.43509 | 143.1 | 0.67544 | 159 | 0.69134 | 151.2 | 0.99603 | 168 | 1.0101
[8 empty] | 122.4 | 0.063563 | 136 | 0.077503 | 124.2 | 0.092421 | 138 | 0.108 | 127.8 | 0.15845 | 142 | 0.17467 | 131.4 | 0.27159 | 146 | 0.28509 | 137.7 | 0.41456 | 153 | 0.42884 | 144 | 0.66673 | 160 | 0.683 | 152.1 | 0.98354 | 169 | 0.99967
[8 empty] | 123.3 | 0.062747 | 137 | 0.077503 | 125.1 | 0.091209 | 139 | 0.108 | 128.7 | 0.15634 | 143 | 0.17328 | 132.3 | 0.26797 | 147 | 0.283 | 138.6 | 0.40914 | 154 | 0.42467 | 144.9 | 0.65818 | 161 | 0.67467 | 153 | 0.97131 | 170 | 0.98509
[8 empty] | 124.2 | 0.061979 | 138 | 0.076797 | 126 | 0.090019 | 140 | 0.1066 | 129.6 | 0.15428 | 144 | 0.16911 | 133.2 | 0.26441 | 148 | 0.27884 | 139.5 | 0.40382 | 155 | 0.41842 | 145.8 | 0.64981 | 162 | 0.66634 | 153.9 | 0.95929 | 171 | 0.97467
[8 empty] | 125.1 | 0.061208 | 139 | 0.076797 | 126.9 | 0.088866 | 141 | 0.1059 | 130.5 | 0.15226 | 145 | 0.16773 | 134.1 | 0.26094 | 149 | 0.27467 | 140.4 | 0.3986 | 156 | 0.41217 | 146.7 | 0.6416 | 163 | 0.658 | 154.8 | 0.94752 | 172 | 0.96217
[8 empty] | 126 | 0.060448 | 140 | 0.076088 | 127.8 | 0.087752 | 142 | 0.1024 | 131.4 | 0.15026 | 146 | 0.16634 | 135 | 0.25753 | 150 | 0.27467 | 141.3 | 0.39351 | 157 | 0.408 | 147.6 | 0.63355 | 164 | 0.64967 | 155.7 | 0.93596 | 173 | 0.94967
[8 empty] | 126.9 | 0.059717 | 141 | 0.076088 | 128.7 | 0.086651 | 143 | 0.1017 | 132.3 | 0.14833 | 147 | 0.16495 | 135.9 | 0.25419 | 151 | 0.26842 | 142.2 | 0.38851 | 158 | 0.40175 | 148.5 | 0.62566 | 165 | 0.64134 | 156.6 | 0.92462 | 174 | 0.94134
[8 empty] | 127.8 | 0.059013 | 142 | 0.07466 | 129.6 | 0.085565 | 144 | 0.1011 | 133.2 | 0.14644 | 148 | 0.16078 | 136.8 | 0.25091 | 152 | 0.26634 | 143.1 | 0.38361 | 159 | 0.39967 | 149.4 | 0.61793 | 166 | 0.633 | 157.5 | 0.91349 | 175 | 0.92675
[8 empty] | 128.7 | 0.058321 | 143 | 0.07466 | 130.5 | 0.084503 | 145 | 0.0997 | 134.1 | 0.14457 | 149 | 0.16009 | 137.7 | 0.24771 | 153 | 0.26217 | 144 | 0.37879 | 160 | 0.39342 | 150.3 | 0.61034 | 167 | 0.62467 | 158.4 | 0.90257 | 176 | 0.91634
[8 empty] | 129.6 | 0.057635 | 144 | 0.074661 | 131.4 | 0.083457 | 146 | 0.0997 | 135 | 0.14274 | 150 | 0.158 | 138.6 | 0.24457 | 154 | 0.258 | 144.9 | 0.37407 | 161 | 0.39134 | 151.2 | 0.60289 | 168 | 0.61634 | 159.3 | 0.89185 | 177 | 0.908
[8 empty] | 130.5 | 0.056964 | 145 | 0.07466 | 132.3 | 0.082446 | 147 | 0.0997 | 135.9 | 0.14097 | 151 | 0.158 | 139.5 | 0.24149 | 155 | 0.258 | 145.8 | 0.36943 | 162 | 0.383 | 152.1 | 0.59556 | 169 | 0.61009 | 160.2 | 0.88133 | 178 | 0.8955
[8 empty] | 131.4 | 0.056289 | 146 | 0.073231 | 133.2 | 0.081455 | 148 | 0.0983 | 136.8 | 0.13921 | 152 | 0.15661 | 140.4 | 0.23845 | 156 | 0.25175 | 146.7 | 0.3649 | 163 | 0.37884 | 153 | 0.5884 | 170 | 0.60175 | 161.1 | 0.87099 | 179 | 0.88509
[8 empty] | 132.3 | 0.055657 | 147 | 0.07323 | 134.1 | 0.08047 | 149 | 0.0976 | 137.7 | 0.1375 | 153 | 0.15245 | 141.3 | 0.2355 | 157 | 0.24967 | 147.6 | 0.36045 | 164 | 0.37467 | 153.9 | 0.58134 | 171 | 0.5955 | 162 | 0.86084 | 180 | 0.87467
[8 empty] | 133.2 | 0.055027 | 148 | 0.069033 | 135 | 0.079515 | 150 | 0.0941 | 138.6 | 0.13581 | 154 | 0.15106 | 142.2 | 0.2326 | 158 | 0.24967 | 148.5 | 0.35609 | 165 | 0.3705 | 154.8 | 0.57443 | 172 | 0.59134 | 162.9 | 0.85087 | 181 | 0.86634
[8 empty] | 134.1 | 0.054402 | 149 | 0.069033 | 135.9 | 0.078585 | 151 | 0.0934 | 139.5 | 0.13418 | 155 | 0.14967 | 143.1 | 0.22976 | 159 | 0.24342 | 149.4 | 0.35181 | 166 | 0.36634 | 155.7 | 0.56764 | 173 | 0.583 | 163.8 | 0.84111 | 182 | 0.858
[8 empty] | 135 | 0.053797 | 150 | 0.068355 | 136.8 | 0.077657 | 152 | 0.0927 | 140.4 | 0.13255 | 156 | 0.14967 | 144 | 0.22695 | 160 | 0.24134 | 150.3 | 0.34761 | 167 | 0.36217 | 156.6 | 0.56097 | 174 | 0.57467 | 164.7 | 0.83149 | 183 | 0.8455
[8 empty] | 135.9 | 0.053208 | 151 | 0.068355 | 137.7 | 0.076771 | 153 | 0.0927 | 141.3 | 0.13098 | 157 | 0.14828 | 144.9 | 0.22422 | 161 | 0.24134 | 151.2 | 0.34349 | 168 | 0.358 | 157.5 | 0.55441 | 175 | 0.56842 | 165.6 | 0.82203 | 184 | 0.83509
[8 empty] | 136.8 | 0.052611 | 152 | 0.067683 | 138.6 | 0.075877 | 154 | 0.0913 | 142.2 | 0.12941 | 158 | 0.14412 | 145.8 | 0.22152 | 162 | 0.23509 | 152.1 | 0.33943 | 169 | 0.35384 | 158.4 | 0.548 | 176 | 0.56217 | 166.5 | 0.81275 | 185 | 0.82675
[8 empty] | 137.7 | 0.052063 | 153 | 0.067683 | 139.5 | 0.075019 | 155 | 0.0913 | 143.1 | 0.12789 | 159 | 0.14342 | 146.7 | 0.21888 | 163 | 0.233 | 153 | 0.33545 | 170 | 0.34967 | 159.3 | 0.54168 | 177 | 0.558 | 167.4 | 0.80362 | 186 | 0.81842
[8 empty] | 138.6 | 0.05149 | 154 | 0.067683 | 140.4 | 0.074172 | 156 | 0.0913 | 144 | 0.1264 | 160 | 0.14273 | 147.6 | 0.2163 | 164 | 0.233 | 153.9 | 0.33154 | 171 | 0.3455 | 160.2 | 0.53548 | 178 | 0.54967 | 168.3 | 0.79465 | 187 | 0.808
[8 empty] | 139.5 | 0.050952 | 155 | 0.066351 | 141.3 | 0.07335 | 157 | 0.0899 | 144.9 | 0.12493 | 161 | 0.14134 | 148.5 | 0.21376 | 165 | 0.22675 | 154.8 | 0.3277 | 172 | 0.34134 | 161.1 | 0.52939 | 179 | 0.54342 | 169.2 | 0.78585 | 188 | 0.79967
[8 empty] | 140.4 | 0.050406 | 156 | 0.066351 | 142.2 | 0.072512 | 158 | 0.0899 | 145.8 | 0.12349 | 162 | 0.13995 | 149.4 | 0.21127 | 166 | 0.22467 | 155.7 | 0.32393 | 173 | 0.34134 | 162 | 0.5234 | 180 | 0.53717 | 170.1 | 0.77719 | 189 | 0.79134
[8 empty] | 141.3 | 0.049893 | 157 | 0.066351 | 143.1 | 0.071724 | 159 | 0.0857 | 146.7 | 0.12206 | 163 | 0.13578 | 150.3 | 0.20883 | 167 | 0.22467 | 156.6 | 0.32022 | 174 | 0.33509 | 162.9 | 0.51752 | 181 | 0.533 | 171 | 0.76868 | 190 | 0.783
[8 empty] | 142.2 | 0.049356 | 158 | 0.066351 | 144 | 0.070944 | 160 | 0.0857 | 147.6 | 0.12067 | 164 | 0.13508 | 151.2 | 0.20643 | 168 | 0.2205 | 157.5 | 0.31659 | 175 | 0.333 | 163.8 | 0.51176 | 182 | 0.52675 | 171.9 | 0.76031 | 191 | 0.77467
[8 empty] | 143.1 | 0.048859 | 159 | 0.066351 | 144.9 | 0.070172 | 161 | 0.0851 | 148.5 | 0.11931 | 165 | 0.13439 | 152.1 | 0.20406 | 169 | 0.21842 | 158.4 | 0.31302 | 176 | 0.32675 | 164.7 | 0.50607 | 183 | 0.5205 | 172.8 | 0.75208 | 192 | 0.76634
[8 empty] | 144 | 0.048368 | 160 | 0.065023 | 145.8 | 0.069411 | 162 | 0.0844 | 149.4 | 0.11798 | 166 | 0.133 | 153 | 0.20175 | 170 | 0.21634 | 159.3 | 0.30951 | 177 | 0.32467 | 165.6 | 0.50048 | 184 | 0.51634 | 173.7 | 0.74399 | 193 | 0.758
[8 empty] | 144.9 | 0.047877 | 161 | 0.065023 | 146.7 | 0.06866 | 163 | 0.0844 | 150.3 | 0.11666 | 167 | 0.133 | 153.9 | 0.19946 | 171 | 0.21634 | 160.2 | 0.30607 | 178 | 0.3205 | 166.5 | 0.49499 | 185 | 0.51009 | 174.6 | 0.73602 | 194 | 0.74967
[8 empty] | 145.8 | 0.047395 | 162 | 0.065023 | 147.6 | 0.067928 | 164 | 0.083 | 151.2 | 0.11538 | 168 | 0.133 | 154.8 | 0.19723 | 172 | 0.21009 | 161.1 | 0.30267 | 179 | 0.31634 | 167.4 | 0.48959 | 186 | 0.50384 | 175.5 | 0.7282 | 195 | 0.74342
[8 empty] | 146.7 | 0.046915 | 163 | 0.06231 | 148.5 | 0.067215 | 165 | 0.083 | 152.1 | 0.11411 | 169 | 0.13162 | 155.7 | 0.19502 | 173 | 0.21009 | 162 | 0.29934 | 180 | 0.31634 | 168.3 | 0.48428 | 187 | 0.49967 | 176.4 | 0.72048 | 196 | 0.73509
[8 empty] | 147.6 | 0.046453 | 164 | 0.060901 | 149.4 | 0.066521 | 166 | 0.083 | 153 | 0.11287 | 170 | 0.12745 | 156.6 | 0.19256 | 174 | 0.208 | 162.9 | 0.29606 | 181 | 0.31009 | 169.2 | 0.47907 | 188 | 0.49342 | 177.3 | 0.71292 | 197 | 0.72675
[8 empty] | 148.5 | 0.045999 | 165 | 0.060901 | 150.3 | 0.065818 | 167 | 0.083 | 153.9 | 0.11164 | 171 | 0.12676 | 157.5 | 0.19044 | 175 | 0.208 | 163.8 | 0.29287 | 182 | 0.308 | 170.1 | 0.47395 | 189 | 0.49134 | 178.2 | 0.70546 | 198 | 0.71842
[8 empty] | 149.4 | 0.045557 | 166 | 0.060182 | 151.2 | 0.065144 | 168 | 0.0816 | 154.8 | 0.11045 | 172 | 0.12606 | 158.4 | 0.18837 | 176 | 0.20245 | 164.7 | 0.2897 | 183 | 0.30384 | 171 | 0.46889 | 190 | 0.483 | 179.1 | 0.69812 | 199 | 0.71217
[8 empty] | 150.3 | 0.045105 | 500 | 0.05 | 152.1 | 0.064486 | 169 | 0.0816 | 155.7 | 0.10926 | 173 | 0.12467 | 159.3 | 0.18632 | 177 | 0.20175 | 165.6 | 0.28658 | 184 | 0.30175 | 171.9 | 0.46393 | 191 | 0.47675 | 180 | 0.69091 | 200 | 0.708
[8 empty] | 151.2 | 0.044681 | 500 | 0.033 | 153 | 0.063831 | 170 | 0.0816 | 156.6 | 0.10811 | 174 | 0.12467 | 160.2 | 0.18432 | 178 | 0.19967 | 166.5 | 0.28352 | 185 | 0.29967 | 172.8 | 0.45904 | 192 | 0.47467 | 180.9 | 0.68382 | 201 | 0.69967
[8 empty] | 152.1 | 0.044263 | 1000 | 0.033 | 153.9 | 0.063182 | 171 | 0.0775 | 157.5 | 0.10697 | 175 | 0.12467 | 161.1 | 0.18232 | 179 | 0.19967 | 167.4 | 0.28052 | 186 | 0.29342 | 173.7 | 0.45424 | 193 | 0.46842 | 181.8 | 0.67683 | 202 | 0.69134
[8 empty] | 153 | 0.043856 | 6300 | 0.022 | 154.8 | 0.062555 | 172 | 0.0775 | 158.4 | 0.10585 | 176 | 0.12328 | 162 | 0.18039 | 180 | 0.19411 | 168.3 | 0.27754 | 187 | 0.29134 | 174.6 | 0.44951 | 194 | 0.46634 | 182.7 | 0.66995 | 203 | 0.68509
[8 empty] | 153.9 | 0.043438 |  |  | 155.7 | 0.061932 | 173 | 0.0768 | 159.3 | 0.10476 | 177 | 0.11911 | 162.9 | 0.17847 | 181 | 0.19342 | 169.2 | 0.27464 | 188 | 0.29134 | 175.5 | 0.44487 | 195 | 0.46009 | 183.6 | 0.66317 | 204 | 0.67675
[8 empty] | 154.8 | 0.043042 |  |  | 156.6 | 0.061318 | 174 | 0.0768 | 160.2 | 0.10368 | 178 | 0.11841 | 163.8 | 0.17659 | 182 | 0.19273 | 170.1 | 0.27179 | 189 | 0.28509 | 176.4 | 0.44027 | 196 | 0.45384 | 184.5 | 0.65651 | 205 | 0.6705
[8 empty] | 155.7 | 0.042648 |  |  | 157.5 | 0.060725 | 175 | 0.0761 | 161.1 | 0.10261 | 179 | 0.11772 | 164.7 | 0.17475 | 183 | 0.19134 | 171 | 0.26897 | 190 | 0.283 | 177.3 | 0.43578 | 197 | 0.44967 | 185.4 | 0.64993 | 206 | 0.66634
[8 empty] | 156.6 | 0.042263 |  |  | 158.4 | 0.060141 | 176 | 0.0761 | 162 | 0.10157 | 180 | 0.11772 | 165.6 | 0.17291 | 184 | 0.18995 | 171.9 | 0.26619 | 191 | 0.283 | 178.2 | 0.43134 | 198 | 0.4455 | 186.3 | 0.64348 | 207 | 0.658
[8 empty] | 250.2 | 0.038 |  |  | 159.3 | 0.05957 | 177 | 0.0747 | 162.9 | 0.10054 | 181 | 0.11634 | 166.5 | 0.17113 | 185 | 0.18578 | 172.8 | 0.26347 | 192 | 0.27675 | 179.1 | 0.42698 | 199 | 0.44134 | 187.2 | 0.63711 | 208 | 0.65175
[8 empty] | 250.2 | 0.0072687 |  |  | 160.2 | 0.059005 | 178 | 0.0747 | 163.8 | 0.099527 | 182 | 0.11634 | 167.4 | 0.16938 | 186 | 0.18439 | 173.7 | 0.26079 | 193 | 0.27467 | 180 | 0.42268 | 200 | 0.43717 | 188.1 | 0.63084 | 209 | 0.6455
[8 empty] | 468 | 0.003 |  |  | 161.1 | 0.058434 | 179 | 0.0747 | 164.7 | 0.098545 | 183 | 0.11496 | 168.3 | 0.16765 | 187 | 0.183 | 174.6 | 0.25815 | 194 | 0.27467 | 180.9 | 0.41846 | 201 | 0.433 | 189 | 0.62466 | 210 | 0.64134
[8 empty] | 6300 | 0.003 |  |  | 162 | 0.057895 | 180 | 0.0747 | 165.6 | 0.097553 | 184 | 0.11496 | 169.2 | 0.16593 | 188 | 0.183 | 175.5 | 0.25555 | 195 | 0.26842 | 181.8 | 0.4143 | 202 | 0.42884 | 189.9 | 0.61859 | 211 | 0.633
[12 empty] | 162.9 | 0.057353 | 181 | 0.0747 | 166.5 | 0.096601 | 185 | 0.11079 | 170.1 | 0.16426 | 189 | 0.18161 | 176.4 | 0.25299 | 196 | 0.26634 | 182.7 | 0.4102 | 203 | 0.42467 | 190.8 | 0.6126 | 212 | 0.62675
[12 empty] | 163.8 | 0.056819 | 182 | 0.0732 | 167.4 | 0.095655 | 186 | 0.1101 | 171 | 0.16261 | 190 | 0.17745 | 177.3 | 0.25048 | 197 | 0.26634 | 183.6 | 0.40616 | 204 | 0.4205 | 191.7 | 0.6067 | 213 | 0.6205
[12 empty] | 164.7 | 0.056299 | 183 | 0.0732 | 168.3 | 0.094728 | 187 | 0.1101 | 171.9 | 0.16099 | 191 | 0.17606 | 178.2 | 0.24798 | 198 | 0.26217 | 184.5 | 0.40218 | 205 | 0.41634 | 192.6 | 0.60088 | 214 | 0.61634
[12 empty] | 165.6 | 0.055776 | 184 | 0.0732 | 169.2 | 0.093799 | 188 | 0.1094 | 172.8 | 0.15938 | 192 | 0.17467 | 179.1 | 0.24555 | 199 | 0.26009 | 185.4 | 0.39825 | 206 | 0.41217 | 193.5 | 0.59515 | 215 | 0.61009
[12 empty] | 166.5 | 0.055275 | 185 | 0.069 | 170.1 | 0.092896 | 189 | 0.108 | 173.7 | 0.1578 | 193 | 0.17467 | 180 | 0.24314 | 200 | 0.258 | 186.3 | 0.3944 | 207 | 0.408 | 194.4 | 0.5895 | 216 | 0.60384
[12 empty] | 167.4 | 0.054778 | 186 | 0.069 | 171 | 0.092009 | 190 | 0.108 | 174.6 | 0.15627 | 194 | 0.17328 | 180.9 | 0.24079 | 201 | 0.258 | 187.2 | 0.3906 | 208 | 0.408 | 195.3 | 0.58394 | 217 | 0.59967
[12 empty] | 168.3 | 0.054292 | 187 | 0.069 | 171.9 | 0.091139 | 191 | 0.108 | 175.5 | 0.15475 | 195 | 0.16911 | 181.8 | 0.23846 | 202 | 0.25175 | 188.1 | 0.38686 | 209 | 0.40175 | 196.2 | 0.57846 | 218 | 0.59342
[12 empty] | 169.2 | 0.053803 | 188 | 0.0684 | 172.8 | 0.090272 | 192 | 0.108 | 176.4 | 0.15326 | 196 | 0.16842 | 182.7 | 0.23617 | 203 | 0.24967 | 189 | 0.38316 | 210 | 0.39967 | 197.1 | 0.57306 | 219 | 0.58717
[12 empty] | 170.1 | 0.053321 | 189 | 0.0684 | 173.7 | 0.089425 | 193 | 0.1066 | 177.3 | 0.15179 | 197 | 0.16773 | 183.6 | 0.2339 | 204 | 0.24967 | 189.9 | 0.37954 | 211 | 0.39342 | 198 | 0.56774 | 220 | 0.583
[12 empty] | 171 | 0.052863 | 190 | 0.0677 | 174.6 | 0.088602 | 194 | 0.10243 | 178.2 | 0.15033 | 198 | 0.16634 | 184.5 | 0.23168 | 205 | 0.2455 | 190.8 | 0.37596 | 212 | 0.39134 | 198.9 | 0.56249 | 221 | 0.57675
[12 empty] | 171.9 | 0.052403 | 191 | 0.0677 | 175.5 | 0.087795 | 195 | 0.10243 | 179.1 | 0.14889 | 199 | 0.16634 | 185.4 | 0.22946 | 206 | 0.24342 | 191.7 | 0.37244 | 213 | 0.38717 | 199.8 | 0.55732 | 222 | 0.57467
[12 empty] | 172.8 | 0.051947 | 192 | 0.0677 | 176.4 | 0.086981 | 196 | 0.10174 | 180 | 0.14748 | 200 | 0.16495 | 186.3 | 0.22732 | 207 | 0.24134 | 192.6 | 0.36895 | 214 | 0.383 | 200.7 | 0.55221 | 223 | 0.56634
[12 empty] | 173.7 | 0.051491 | 193 | 0.0677 | 177.3 | 0.086198 | 197 | 0.10105 | 180.9 | 0.1461 | 201 | 0.16078 | 187.2 | 0.22519 | 208 | 0.24134 | 193.5 | 0.36553 | 215 | 0.383 | 201.6 | 0.54719 | 224 | 0.56009
[12 empty] | 174.6 | 0.051059 | 194 | 0.0664 | 178.2 | 0.085412 | 198 | 0.10105 | 181.8 | 0.14472 | 202 | 0.16009 | 188.1 | 0.22309 | 209 | 0.23717 | 194.4 | 0.36214 | 216 | 0.37675 | 202.5 | 0.54223 | 225 | 0.558
[12 empty] | 175.5 | 0.050642 | 195 | 0.0664 | 179.1 | 0.084636 | 199 | 0.099673 | 182.7 | 0.14338 | 203 | 0.15939 | 189 | 0.22101 | 210 | 0.23509 | 195.3 | 0.35881 | 217 | 0.37467 | 203.4 | 0.53735 | 226 | 0.55175
[12 empty] | 176.4 | 0.050217 | 196 | 0.0664 | 180 | 0.083874 | 200 | 0.099673 | 183.6 | 0.14206 | 204 | 0.158 | 189.9 | 0.21899 | 211 | 0.233 | 196.2 | 0.35552 | 218 | 0.36842 | 204.3 | 0.53253 | 227 | 0.54967
[12 empty] | 177.3 | 0.049805 | 197 | 0.0664 | 180.9 | 0.083133 | 201 | 0.099673 | 184.5 | 0.14074 | 205 | 0.158 | 190.8 | 0.21698 | 212 | 0.233 | 197.1 | 0.35229 | 219 | 0.36634 | 205.2 | 0.52779 | 228 | 0.54134
[12 empty] | 178.2 | 0.049389 | 198 | 0.0664 | 181.8 | 0.082397 | 202 | 0.099673 | 185.4 | 0.13946 | 206 | 0.15661 | 191.7 | 0.215 | 213 | 0.22884 | 198 | 0.3491 | 220 | 0.36634 | 206.1 | 0.52309 | 229 | 0.53717
[12 empty] | 179.1 | 0.048973 | 199 | 0.0664 | 182.7 | 0.081666 | 203 | 0.098297 | 186.3 | 0.13818 | 207 | 0.15245 | 192.6 | 0.21305 | 214 | 0.22675 | 198.9 | 0.34596 | 221 | 0.36009 | 207 | 0.51846 | 230 | 0.533
[12 empty] | 180 | 0.048572 | 200 | 0.0664 | 183.6 | 0.080962 | 204 | 0.098297 | 187.2 | 0.13694 | 208 | 0.15175 | 193.5 | 0.21112 | 215 | 0.22467 | 199.8 | 0.34286 | 222 | 0.358 | 207.9 | 0.5139 | 231 | 0.52675
[12 empty] | 180.9 | 0.048191 | 201 | 0.065 | 184.5 | 0.080254 | 205 | 0.09414 | 188.1 | 0.13571 | 209 | 0.15106 | 194.4 | 0.20922 | 216 | 0.22467 | 200.7 | 0.33979 | 223 | 0.35384 | 208.8 | 0.50939 | 232 | 0.52467
[12 empty] | 181.8 | 0.047796 | 202 | 0.065 | 185.4 | 0.079554 | 206 | 0.09414 | 189 | 0.13448 | 210 | 0.14967 | 195.3 | 0.20735 | 217 | 0.22467 | 201.6 | 0.33677 | 224 | 0.35175 | 209.7 | 0.50494 | 233 | 0.51842
[12 empty] | 182.7 | 0.047414 | 203 | 0.065 | 186.3 | 0.078869 | 207 | 0.09344 | 189.9 | 0.13329 | 211 | 0.14967 | 196.2 | 0.20551 | 218 | 0.21842 | 202.5 | 0.3338 | 225 | 0.34967 | 210.6 | 0.50056 | 234 | 0.51634
[12 empty] | 183.6 | 0.04705 | 204 | 0.0644 | 187.2 | 0.078204 | 208 | 0.09344 | 190.8 | 0.13211 | 212 | 0.14967 | 197.1 | 0.20369 | 219 | 0.21842 | 203.4 | 0.33087 | 226 | 0.3455 | 211.5 | 0.49624 | 235 | 0.51009
[12 empty] | 184.5 | 0.046672 | 205 | 0.0609 | 188.1 | 0.077536 | 209 | 0.092739 | 191.7 | 0.13094 | 213 | 0.14828 | 198 | 0.20191 | 220 | 0.21634 | 204.3 | 0.32798 | 227 | 0.34134 | 212.4 | 0.49198 | 236 | 0.508
[12 empty] | 185.4 | 0.046302 | 206 | 0.0609 | 189 | 0.076876 | 210 | 0.092739 | 192.6 | 0.12979 | 214 | 0.14412 | 198.9 | 0.20014 | 221 | 0.21634 | 205.2 | 0.32513 | 228 | 0.34134 | 213.3 | 0.48778 | 237 | 0.50175
[12 empty] | 186.3 | 0.045939 | 207 | 0.0609 | 189.9 | 0.076242 | 211 | 0.091333 | 193.5 | 0.12867 | 215 | 0.14342 | 199.8 | 0.1984 | 222 | 0.21217 | 206.1 | 0.32231 | 229 | 0.33509 | 214.2 | 0.48363 | 238 | 0.49967
[12 empty] | 187.2 | 0.045593 | 208 | 0.0609 | 190.8 | 0.075594 | 212 | 0.091332 | 194.4 | 0.12754 | 216 | 0.14273 | 200.7 | 0.19667 | 223 | 0.21009 | 207 | 0.31953 | 230 | 0.333 | 215.1 | 0.47952 | 239 | 0.49342
[12 empty] | 188.1 | 0.045244 | 209 | 0.0602 | 191.7 | 0.074973 | 213 | 0.091332 | 195.3 | 0.12644 | 217 | 0.14273 | 201.6 | 0.1947 | 224 | 0.21009 | 207.9 | 0.31679 | 231 | 0.333 | 216 | 0.47548 | 240 | 0.49134
[12 empty] | 189 | 0.044886 | 210 | 0.0602 | 192.6 | 0.074353 | 214 | 0.091333 | 196.2 | 0.12536 | 218 | 0.14134 | 202.5 | 0.19303 | 225 | 0.20939 | 208.8 | 0.31408 | 232 | 0.32675 | 216.9 | 0.47148 | 241 | 0.48509
[12 empty] | 189.9 | 0.044553 | 211 | 0.0602 | 193.5 | 0.073746 | 215 | 0.091332 | 197.1 | 0.1243 | 219 | 0.14134 | 203.4 | 0.19138 | 226 | 0.208 | 209.7 | 0.3114 | 233 | 0.32467 | 217.8 | 0.46754 | 242 | 0.483
[12 empty] | 190.8 | 0.044214 | 500 | 0.051 | 194.4 | 0.073136 | 216 | 0.089925 | 198 | 0.12323 | 220 | 0.13995 | 204.3 | 0.18974 | 227 | 0.20661 | 210.6 | 0.30876 | 234 | 0.32467 | 218.7 | 0.46365 | 243 | 0.47675
[12 empty] | 191.7 | 0.043892 | 500 | 0.033 | 195.3 | 0.072548 | 217 | 0.089925 | 198.9 | 0.12221 | 221 | 0.13925 | 205.2 | 0.18815 | 228 | 0.20245 | 211.5 | 0.30617 | 235 | 0.3205 | 219.6 | 0.45982 | 244 | 0.47467
[12 empty] | 192.6 | 0.043554 | 1000 | 0.033 | 196.2 | 0.071961 | 218 | 0.085744 | 199.8 | 0.12117 | 222 | 0.13578 | 206.1 | 0.18655 | 229 | 0.20175 | 212.4 | 0.3036 | 236 | 0.31842 | 220.5 | 0.45602 | 245 | 0.4705
[12 empty] | 193.5 | 0.043237 | 6300 | 0.022 | 197.1 | 0.071399 | 219 | 0.085744 | 200.7 | 0.12016 | 223 | 0.13508 | 207 | 0.18499 | 230 | 0.20106 | 213.3 | 0.30107 | 237 | 0.31634 | 221.4 | 0.45228 | 246 | 0.46634
[12 empty] | 194.4 | 0.042916 |  |  | 198 | 0.070814 | 220 | 0.085744 | 201.6 | 0.11915 | 224 | 0.13439 | 207.9 | 0.18345 | 231 | 0.19967 | 214.2 | 0.29857 | 238 | 0.31217 | 222.3 | 0.44859 | 247 | 0.46217
[12 empty] | 195.3 | 0.0426 |  |  | 198.9 | 0.070266 | 221 | 0.085057 | 202.5 | 0.11818 | 225 | 0.13439 | 208.8 | 0.18193 | 232 | 0.19967 | 215.1 | 0.29611 | 239 | 0.31009 | 223.2 | 0.44495 | 248 | 0.46009
[12 empty] | 250.2 | 0.039964 |  |  | 199.8 | 0.069712 | 222 | 0.085057 | 203.4 | 0.11721 | 226 | 0.133 | 209.7 | 0.18042 | 233 | 0.19759 | 216 | 0.29366 | 240 | 0.308 | 224.1 | 0.44134 | 249 | 0.458
[12 empty] | 250.2 | 0.0072687 |  |  | 200.7 | 0.06916 | 223 | 0.084373 | 204.3 | 0.11624 | 227 | 0.133 | 210.6 | 0.17895 | 234 | 0.19342 | 216.9 | 0.29126 | 241 | 0.308 | 225 | 0.43778 | 250 | 0.45175
[12 empty] | 468 | 0.003 |  |  | 201.6 | 0.068614 | 224 | 0.084373 | 205.2 | 0.1153 | 228 | 0.133 | 211.5 | 0.17748 | 235 | 0.19273 | 217.8 | 0.28889 | 242 | 0.30175 | 225.9 | 0.43427 | 251 | 0.44967
[12 empty] | 6300 | 0.003 |  |  | 202.5 | 0.068089 | 225 | 0.084373 | 206.1 | 0.11436 | 229 | 0.13162 | 212.4 | 0.17604 | 236 | 0.19134 | 218.7 | 0.28654 | 243 | 0.30175 | 226.8 | 0.43079 | 252 | 0.4455
[16 empty] | 203.4 | 0.067569 | 226 | 0.08301 | 207 | 0.11344 | 230 | 0.12745 | 213.3 | 0.17461 | 237 | 0.19134 | 219.6 | 0.28423 | 244 | 0.29967 | 227.7 | 0.42736 | 253 | 0.44134
[16 empty] | 204.3 | 0.067039 | 227 | 0.08301 | 207.9 | 0.11252 | 231 | 0.12745 | 214.2 | 0.1732 | 238 | 0.18995 | 220.5 | 0.28194 | 245 | 0.2955 | 228.6 | 0.42398 | 254 | 0.44134
[16 empty] | 205.2 | 0.066535 | 228 | 0.08301 | 208.8 | 0.11164 | 232 | 0.12676 | 215.1 | 0.17181 | 239 | 0.18578 | 221.4 | 0.27969 | 246 | 0.29342 | 229.5 | 0.42064 | 255 | 0.43509
[16 empty] | 206.1 | 0.06603 | 229 | 0.08301 | 209.7 | 0.11074 | 233 | 0.12606 | 216 | 0.17045 | 240 | 0.18509 | 222.3 | 0.27746 | 247 | 0.29134 | 230.4 | 0.41733 | 256 | 0.433
[16 empty] | 207 | 0.065532 | 230 | 0.08301 | 210.6 | 0.10987 | 234 | 0.12606 | 216.9 | 0.16909 | 241 | 0.18439 | 223.2 | 0.27526 | 248 | 0.29134 | 231.3 | 0.41408 | 257 | 0.42675
[16 empty] | 207.9 | 0.065036 | 231 | 0.081649 | 211.5 | 0.10901 | 235 | 0.12467 | 217.8 | 0.16774 | 242 | 0.183 | 224.1 | 0.27309 | 249 | 0.28717 | 232.2 | 0.41084 | 258 | 0.42467
[16 empty] | 208.8 | 0.064561 | 232 | 0.081649 | 212.4 | 0.10817 | 236 | 0.12467 | 218.7 | 0.16643 | 243 | 0.183 | 225 | 0.27094 | 250 | 0.28509 | 233.1 | 0.40766 | 259 | 0.42467
[16 empty] | 209.7 | 0.064072 | 233 | 0.081649 | 213.3 | 0.10732 | 237 | 0.12467 | 219.6 | 0.16513 | 244 | 0.18162 | 225.9 | 0.26882 | 251 | 0.283 | 234 | 0.40451 | 260 | 0.41842
[16 empty] | 210.6 | 0.063609 | 234 | 0.077503 | 214.2 | 0.10649 | 238 | 0.12328 | 220.5 | 0.16383 | 245 | 0.18092 | 226.8 | 0.26672 | 252 | 0.283 | 234.9 | 0.40141 | 261 | 0.41634
[16 empty] | 211.5 | 0.06314 | 235 | 0.077503 | 215.1 | 0.10567 | 239 | 0.12328 | 221.4 | 0.16255 | 246 | 0.17745 | 227.7 | 0.26465 | 253 | 0.27884 | 235.8 | 0.39832 | 262 | 0.41217
[16 empty] | 212.4 | 0.062697 | 236 | 0.077503 | 216 | 0.10487 | 240 | 0.11911 | 222.3 | 0.16131 | 247 | 0.17675 | 228.6 | 0.26261 | 254 | 0.27675 | 236.7 | 0.3953 | 263 | 0.41009
[16 empty] | 213.3 | 0.062229 | 237 | 0.076797 | 216.9 | 0.10406 | 241 | 0.11841 | 223.2 | 0.16007 | 248 | 0.17606 | 229.5 | 0.26059 | 255 | 0.27467 | 237.6 | 0.39229 | 264 | 0.408
[16 empty] | 214.2 | 0.061788 | 238 | 0.076797 | 217.8 | 0.10326 | 242 | 0.11841 | 224.1 | 0.15884 | 249 | 0.17467 | 230.4 | 0.25859 | 256 | 0.27467 | 238.5 | 0.38933 | 265 | 0.40384
[16 empty] | 215.1 | 0.061342 | 239 | 0.076797 | 218.7 | 0.10249 | 243 | 0.11772 | 225 | 0.15763 | 250 | 0.17467 | 231.3 | 0.25663 | 257 | 0.2705 | 239.4 | 0.3864 | 266 | 0.39967
[16 empty] | 216 | 0.06091 | 240 | 0.076088 | 219.6 | 0.10172 | 244 | 0.11772 | 225.9 | 0.15642 | 251 | 0.17328 | 232.2 | 0.25467 | 258 | 0.26842 | 240.3 | 0.38349 | 267 | 0.39967
[16 empty] | 216.9 | 0.060474 | 241 | 0.076088 | 220.5 | 0.10096 | 245 | 0.11634 | 226.8 | 0.15524 | 252 | 0.16911 | 233.1 | 0.25274 | 259 | 0.26634 | 241.2 | 0.38063 | 268 | 0.39342
[16 empty] | 217.8 | 0.060038 | 242 | 0.076088 | 221.4 | 0.1002 | 246 | 0.11634 | 227.7 | 0.15409 | 253 | 0.16911 | 234 | 0.25084 | 260 | 0.26634 | 242.1 | 0.37779 | 269 | 0.39134
[16 empty] | 218.7 | 0.059624 | 243 | 0.074661 | 222.3 | 0.099469 | 247 | 0.11634 | 228.6 | 0.15293 | 254 | 0.16842 | 234.9 | 0.24896 | 261 | 0.26634 | 243 | 0.375 | 270 | 0.39134
[16 empty] | 219.6 | 0.059215 | 244 | 0.07466 | 223.2 | 0.098739 | 248 | 0.11634 | 229.5 | 0.15178 | 255 | 0.16773 | 235.8 | 0.2471 | 262 | 0.26009 | 243.9 | 0.37223 | 271 | 0.38509
[16 empty] | 220.5 | 0.058803 | 245 | 0.07466 | 224.1 | 0.098003 | 249 | 0.11496 | 230.4 | 0.15066 | 256 | 0.16634 | 236.7 | 0.24527 | 263 | 0.26009 | 244.8 | 0.3695 | 272 | 0.383
[16 empty] | 221.4 | 0.058384 | 246 | 0.074661 | 225 | 0.097296 | 250 | 0.11496 | 231.3 | 0.14955 | 257 | 0.16634 | 237.6 | 0.24345 | 264 | 0.258 | 245.7 | 0.36681 | 273 | 0.383
[16 empty] | 222.3 | 0.057996 | 247 | 0.074661 | 225.9 | 0.096578 | 251 | 0.11079 | 232.2 | 0.14844 | 258 | 0.16495 | 238.5 | 0.24165 | 265 | 0.258 | 246.6 | 0.36414 | 274 | 0.37884
[16 empty] | 223.2 | 0.057606 | 248 | 0.074661 | 226.8 | 0.095882 | 252 | 0.11079 | 233.1 | 0.14735 | 259 | 0.16495 | 239.4 | 0.23989 | 266 | 0.25384 | 247.5 | 0.3615 | 275 | 0.37675
[16 empty] | 224.1 | 0.057209 | 249 | 0.07466 | 227.7 | 0.095203 | 253 | 0.1101 | 234 | 0.14628 | 260 | 0.16078 | 240.3 | 0.23813 | 267 | 0.25175 | 248.4 | 0.35887 | 276 | 0.37467
[16 empty] | 225 | 0.056823 | 250 | 0.073231 | 228.6 | 0.094521 | 254 | 0.1101 | 234.9 | 0.14522 | 261 | 0.16009 | 241.2 | 0.2364 | 268 | 0.24967 | 249.3 | 0.35629 | 277 | 0.3705
[16 empty] | 225.9 | 0.056435 | 251 | 0.073231 | 229.5 | 0.09384 | 255 | 0.1094 | 235.8 | 0.14418 | 262 | 0.15939 | 242.1 | 0.23467 | 269 | 0.24967 | 250.2 | 0.35373 | 278 | 0.36842
[16 empty] | 226.8 | 0.056051 | 252 | 0.073231 | 230.4 | 0.093172 | 256 | 0.1094 | 236.7 | 0.14313 | 263 | 0.15939 | 243 | 0.23298 | 270 | 0.24967 | 250.2 | 0.0072687 | 279 | 0.36634
[16 empty] | 227.7 | 0.055691 | 253 | 0.07323 | 231.3 | 0.092522 | 257 | 0.108 | 237.6 | 0.14212 | 264 | 0.158 | 243.9 | 0.23131 | 271 | 0.2455 | 468 | 0.003 | 280 | 0.36217
[16 empty] | 228.6 | 0.055319 | 254 | 0.069033 | 232.2 | 0.091861 | 258 | 0.108 | 238.5 | 0.14111 | 265 | 0.158 | 244.8 | 0.22965 | 272 | 0.24342 | 6300 | 0.003 | 281 | 0.36009
[16 empty] | 229.5 | 0.054957 | 255 | 0.069033 | 233.1 | 0.091216 | 259 | 0.108 | 239.4 | 0.1401 | 266 | 0.15661 | 245.7 | 0.22802 | 273 | 0.24134 |  |  | 282 | 0.358
[16 empty] | 230.4 | 0.054591 | 256 | 0.069033 | 234 | 0.090589 | 260 | 0.108 | 240.3 | 0.13911 | 267 | 0.15661 | 246.6 | 0.22641 | 274 | 0.24134 |  |  | 283 | 0.358
[16 empty] | 231.3 | 0.054249 | 257 | 0.069033 | 234.9 | 0.089958 | 261 | 0.1066 | 241.2 | 0.13814 | 268 | 0.15245 | 247.5 | 0.22481 | 275 | 0.24134 |  |  | 284 | 0.35175
[16 empty] | 232.2 | 0.053889 | 258 | 0.068355 | 235.8 | 0.089349 | 262 | 0.1066 | 242.1 | 0.13716 | 269 | 0.15175 | 248.4 | 0.22321 | 276 | 0.23717 |  |  | 285 | 0.35175
[16 empty] | 233.1 | 0.053534 | 259 | 0.068355 | 236.7 | 0.08873 | 263 | 0.10243 | 243 | 0.1362 | 270 | 0.15175 | 249.3 | 0.22165 | 277 | 0.23509 |  |  | 286 | 0.34967
[16 empty] | 234 | 0.053198 | 260 | 0.068355 | 237.6 | 0.088125 | 264 | 0.10243 | 243.9 | 0.13526 | 271 | 0.15106 | 250.2 | 0.22009 | 278 | 0.23509 |  |  | 287 | 0.3455
[16 empty] | 234.9 | 0.052857 | 261 | 0.067683 | 238.5 | 0.087527 | 265 | 0.10243 | 244.8 | 0.13433 | 272 | 0.14967 | 250.2 | 0.0072687 | 279 | 0.233 |  |  | 288 | 0.34342
[16 empty] | 235.8 | 0.052529 | 262 | 0.067683 | 239.4 | 0.086938 | 266 | 0.10174 | 245.7 | 0.13339 | 273 | 0.14967 | 468 | 0.003 | 280 | 0.233 |  |  | 289 | 0.34134
[16 empty] | 236.7 | 0.052191 | 263 | 0.067683 | 240.3 | 0.086345 | 267 | 0.10174 | 246.6 | 0.13248 | 274 | 0.14967 | 6300 | 0.003 | 281 | 0.233 |  |  | 290 | 0.34134
[16 empty] | 237.6 | 0.051874 | 264 | 0.067683 | 241.2 | 0.085768 | 268 | 0.10105 | 247.5 | 0.13159 | 275 | 0.14828 |  |  | 282 | 0.22675 |  |  | 291 | 0.33717
[16 empty] | 238.5 | 0.051547 | 265 | 0.067683 | 242.1 | 0.085189 | 269 | 0.10105 | 248.4 | 0.13068 | 276 | 0.14828 |  |  | 283 | 0.22675 |  |  | 292 | 0.33509
[16 empty] | 239.4 | 0.051228 | 266 | 0.066351 | 243 | 0.084633 | 270 | 0.099673 | 249.3 | 0.1298 | 277 | 0.14412 |  |  | 284 | 0.22467 |  |  | 293 | 0.333
[16 empty] | 240.3 | 0.050914 | 267 | 0.066351 | 243.9 | 0.084074 | 271 | 0.099673 | 250.2 | 0.12892 | 278 | 0.14342 |  |  | 285 | 0.22467 |  |  | 294 | 0.333
[16 empty] | 241.2 | 0.050598 | 268 | 0.066351 | 244.8 | 0.083517 | 272 | 0.099673 | 250.2 | 0.0072687 | 279 | 0.14342 |  |  | 286 | 0.22467 |  |  | 295 | 0.32675
[16 empty] | 242.1 | 0.05028 | 269 | 0.066351 | 245.7 | 0.082973 | 273 | 0.099673 | 468 | 0.003 | 280 | 0.14273 |  |  | 287 | 0.2205 |  |  | 296 | 0.32675
[16 empty] | 243 | 0.049984 | 270 | 0.066351 | 246.6 | 0.082435 | 274 | 0.099673 | 6300 | 0.003 | 281 | 0.14273 |  |  | 288 | 0.21842 |  |  | 297 | 0.32467
[16 empty] | 243.9 | 0.049684 | 271 | 0.066351 | 247.5 | 0.081897 | 275 | 0.098297 |  |  | 282 | 0.14134 |  |  | 289 | 0.21842 |  |  | 298 | 0.32467
[16 empty] | 244.8 | 0.049387 | 272 | 0.066351 | 248.4 | 0.081364 | 276 | 0.098297 |  |  | 283 | 0.14134 |  |  | 290 | 0.21634 |  |  | 300 | 0.31634
[16 empty] | 245.7 | 0.049085 | 273 | 0.066351 | 249.3 | 0.080843 | 277 | 0.098297 |  |  | 284 | 0.14134 |  |  | 291 | 0.21634 |  |  | 300 | 0.060182
[16 empty] | 246.6 | 0.048796 | 274 | 0.066351 | 250.2 | 0.080327 | 278 | 0.09414 |  |  | 285 | 0.13995 |  |  | 292 | 0.21634 |  |  | 500 | 0.057
[16 empty] | 247.5 | 0.048508 | 275 | 0.065023 | 250.2 | 0.0072687 | 279 | 0.09414 |  |  | 286 | 0.13995 |  |  | 293 | 0.21217 |  |  | 500 | 0.033
[16 empty] | 248.4 | 0.048216 | 276 | 0.065023 | 468 | 0.003 | 280 | 0.09414 |  |  | 287 | 0.13578 |  |  | 294 | 0.21009 |  |  | 1000 | 0.033
[16 empty] | 249.3 | 0.047935 | 277 | 0.065023 | 6300 | 0.003 | 281 | 0.09344 |  |  | 288 | 0.13508 |  |  | 295 | 0.21009 |  |  | 6300 | 0.022
[16 empty] | 250.2 | 0.047659 | 278 | 0.065023 |  |  | 282 | 0.09344 |  |  | 289 | 0.13508 |  |  | 296 | 0.21009
[16 empty] | 250.2 | 0.0072687 | 279 | 0.065023 |  |  | 283 | 0.09344 |  |  | 290 | 0.13439 |  |  | 297 | 0.208
[16 empty] | 468 | 0.003 | 280 | 0.065023 |  |  | 284 | 0.092739 |  |  | 291 | 0.13439 |  |  | 298 | 0.208
[16 empty] | 6300 | 0.003 | 500 | 0.052 |  |  | 285 | 0.092739 |  |  | 292 | 0.133 |  |  | 299 | 0.208
[18 empty] | 500 | 0.033 |  |  | 286 | 0.092739 |  |  | 293 | 0.133 |  |  | 300 | 0.060183
[18 empty] | 1000 | 0.033 |  |  | 287 | 0.091332 |  |  | 294 | 0.133 |  |  | 500 | 0.057
[18 empty] | 6300 | 0.022 |  |  | 288 | 0.091332 |  |  | 295 | 0.133 |  |  | 500 | 0.033
[22 empty] | 289 | 0.091332 |  |  | 296 | 0.13162 |  |  | 1000 | 0.033
[22 empty] | 290 | 0.091332 |  |  | 297 | 0.12745 |  |  | 6300 | 0.022
[22 empty] | 291 | 0.091332 |  |  | 298 | 0.12745
[22 empty] | 292 | 0.091332 |  |  | 299 | 0.12606
[22 empty] | 293 | 0.089925 |  |  | 300 | 0.060901
[22 empty] | 294 | 0.089925 |  |  | 500 | 0.057
[22 empty] | 295 | 0.089925 |  |  | 500 | 0.033
[22 empty] | 296 | 0.085744 |  |  | 1000 | 0.033
[22 empty] | 297 | 0.085744 |  |  | 6300 | 0.022
[22 empty] | 298 | 0.085057
[22 empty] | 299 | 0.085057
[22 empty] | 300 | 0.060183
[22 empty] | 500 | 0.057
[22 empty] | 500 | 0.033
[22 empty] | 1000 | 0.033
[22 empty] | 6300 | 0.022

## S&C "DE" Speed
S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter
S&C "DE" Speed | [11 empty] | S&C "DE" Speed | [11 empty] | S&C "DE" Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025
Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information.
2DE |  |  |  | 3DE |  |  |  | 4DE |  |  |  | 5DE |  |  |  | 7DE |  |  |  | 10DE |  |  |  | 15DE |  |  |  | 20DE
Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s
4 | 238.6084 | 5 | 238.625 | 5 | 242.3823 | 6 | 242.3983 | 7 | 265.9497 | 8 | 265.9663 | 10.8 | 174.4874 | 12 | 174.5024 | 15.3 | 230.0701 | 17 | 230.0858 | 21.6 | 165.1384 | 24 | 165.1524 | 31.5 | 300.0463 | 35 | 300.0608
5 | 107.2297 | 6 | 107.243 | 6 | 115.1292 | 7 | 115.1434 | 8 | 156.4108 | 9 | 156.4247 | 11.7 | 103.6926 | 13 | 103.708 | 16.2 | 120.0714 | 18 | 120.0851 | 22.5 | 115.5697 | 25 | 115.5851 | 32.4 | 123.7091 | 36 | 123.7247 | 42.3 | 300.0462 | 47 | 300.0608
6 | 69.2016 | 7 | 69.216 | 7 | 71.7252 | 8 | 71.7413 | 9 | 107.559 | 10 | 107.5747 | 12.6 | 76.464 | 14 | 76.4768 | 17.1 | 83.4924 | 19 | 83.508 | 23.4 | 89.0677 | 26 | 89.083 | 33.3 | 92.0877 | 37 | 92.1018 | 43.2 | 180.5697 | 48 | 180.5851
7 | 50.246 | 8 | 50.26 | 8 | 51.5892 | 9 | 51.6038 | 9.9 | 80.9018 | 11 | 80.9163 | 13.5 | 60.4028 | 15 | 60.4184 | 18 | 64.6157 | 20 | 64.633 | 24.3 | 73.3376 | 27 | 73.3518 | 34.2 | 75.5816 | 38 | 75.5955 | 44.1 | 113.3219 | 49 | 113.3351
8 | 38.9524 | 9 | 38.966 | 9 | 39.5095 | 10 | 39.5247 | 10.8 | 64.8616 | 12 | 64.8768 | 14.4 | 49.7946 | 16 | 49.8101 | 18.9 | 52.8839 | 21 | 52.8997 | 25.2 | 62.5922 | 28 | 62.608 | 35.1 | 62.8809 | 39 | 62.8934 | 45 | 76.7211 | 50 | 76.7351
9 | 31.4368 | 10 | 31.452 | 9.9 | 31.9518 | 11 | 31.9663 | 11.7 | 53.5581 | 13 | 53.5747 | 15.3 | 41.73 | 17 | 41.7434 | 19.8 | 44.2263 | 22 | 44.2413 | 26.1 | 54.1002 | 29 | 54.1163 | 36 | 53.2364 | 40 | 53.2518 | 45.9 | 55.9252 | 51 | 55.9413
9.9 | 26.2861 | 11 | 26.3 | 10.8 | 26.4206 | 12 | 26.4351 | 12.6 | 45.1453 | 14 | 45.1601 | 16.2 | 35.4494 | 18 | 35.4663 | 20.7 | 38.2494 | 23 | 38.2663 | 27 | 47.7476 | 30 | 47.7622 | 36.9 | 46.5396 | 41 | 46.5538 | 46.8 | 43.8665 | 52 | 43.883
10.8 | 22.1868 | 12 | 22.202 | 11.7 | 22.4962 | 13 | 22.5101 | 13.5 | 39.1017 | 15 | 39.1163 | 17.1 | 30.6276 | 19 | 30.6413 | 21.6 | 33.7949 | 24 | 33.8101 | 27.9 | 42.8663 | 31 | 42.883 | 37.8 | 40.9288 | 42 | 40.9434 | 47.7 | 35.4083 | 53 | 35.4247
11.7 | 19.2157 | 13 | 19.233 | 12.6 | 19.2764 | 14 | 19.2913 | 14.4 | 34.2819 | 16 | 34.2955 | 18 | 26.8768 | 20 | 26.8913 | 22.5 | 30.3916 | 25 | 30.408 | 28.8 | 37.9846 | 32 | 37.9997 | 38.7 | 36.6814 | 43 | 36.6955 | 48.6 | 30.0602 | 54 | 30.0768
12.6 | 16.8722 | 14 | 16.885 | 13.5 | 16.9018 | 15 | 16.9163 | 15.3 | 30.3614 | 17 | 30.3768 | 18.9 | 23.7048 | 21 | 23.7184 | 23.4 | 27.501 | 26 | 27.5163 | 29.7 | 33.1028 | 33 | 33.1163 | 39.6 | 33.3239 | 44 | 33.3413 | 49.5 | 25.8692 | 55 | 25.8851
13.5 | 14.8871 | 15 | 14.902 | 14.4 | 14.9975 | 16 | 15.0122 | 16.2 | 27.2018 | 18 | 27.2163 | 19.8 | 21.1186 | 22 | 21.133 | 24.3 | 24.9041 | 27 | 24.9184 | 30.6 | 30.2017 | 34 | 30.2163 | 40.5 | 30.2725 | 45 | 30.2872 | 50.4 | 22.6426 | 56 | 22.658
14.4 | 13.3393 | 16 | 13.354 | 15.3 | 13.3733 | 17 | 13.3872 | 17.1 | 24.706 | 19 | 24.7205 | 20.7 | 19.2435 | 23 | 19.258 | 25.2 | 22.9479 | 28 | 22.9622 | 31.5 | 27.5377 | 35 | 27.5518 | 41.4 | 27.2298 | 46 | 27.2434 | 51.3 | 19.8231 | 57 | 19.8372
15.3 | 12.0088 | 17 | 12.025 | 16.2 | 12.1307 | 18 | 12.1455 | 18 | 22.5181 | 20 | 22.533 | 21.6 | 17.7523 | 24 | 17.7663 | 26.1 | 21.1456 | 29 | 21.1601 | 32.4 | 25.0027 | 36 | 25.0163 | 42.3 | 25.2637 | 47 | 25.2768 | 52.2 | 17.5756 | 58 | 17.5913
16.2 | 10.9769 | 18 | 10.991 | 17.1 | 10.9944 | 19 | 11.008 | 18.9 | 20.7965 | 21 | 20.8101 | 22.5 | 16.2745 | 25 | 16.2913 | 27 | 19.4648 | 30 | 19.4788 | 33.3 | 23.0892 | 37 | 23.1038 | 43.2 | 23.2976 | 48 | 23.3122 | 53.1 | 15.6597 | 59 | 15.6747
17.1 | 10.0175 | 19 | 10.033 | 18 | 10.0633 | 20 | 10.0768 | 19.8 | 19.0748 | 22 | 19.0913 | 23.4 | 15.0741 | 26 | 15.0913 | 27.9 | 18.1253 | 31 | 18.1413 | 34.2 | 21.1761 | 38 | 21.1913 | 44.1 | 21.3601 | 49 | 21.3747 | 54 | 14.1749 | 60 | 14.1913
18 | 9.2597 | 20 | 9.275 | 18.9 | 9.2054 | 21 | 9.2184 | 20.7 | 17.8217 | 23 | 17.8351 | 24.3 | 14.0808 | 27 | 14.0955 | 28.8 | 16.7861 | 32 | 16.7997 | 35.1 | 19.5908 | 39 | 19.608 | 45 | 19.9938 | 50 | 20.008 | 54.9 | 12.7898 | 61 | 12.8038
18.9 | 8.5345 | 21 | 8.55 | 19.8 | 8.4842 | 22 | 8.4997 | 21.6 | 16.5785 | 24 | 16.5934 | 25.2 | 13.1698 | 28 | 13.1851 | 29.7 | 15.6568 | 33 | 15.6705 | 36 | 18.0247 | 40 | 18.0413 | 45.9 | 18.6273 | 51 | 18.6413 | 55.8 | 11.4771 | 62 | 11.4913
19.8 | 7.8894 | 22 | 7.904 | 20.7 | 7.8172 | 23 | 7.833 | 22.5 | 15.5206 | 25 | 15.5351 | 26.1 | 12.3503 | 29 | 12.3663 | 30.6 | 14.5643 | 34 | 14.5788 | 36.9 | 16.7213 | 41 | 16.7351 | 46.8 | 17.2609 | 52 | 17.2747 | 56.7 | 10.5138 | 63 | 10.5268
20.7 | 7.3404 | 23 | 7.354 | 21.6 | 7.3228 | 24 | 7.3372 | 23.4 | 14.5773 | 26 | 14.5913 | 27 | 11.649 | 30 | 11.6663 | 31.5 | 13.4935 | 35 | 13.508 | 37.8 | 15.5269 | 42 | 15.5413 | 47.7 | 16.273 | 53 | 16.2872 | 57.6 | 9.5947 | 64 | 9.6101
21.6 | 6.8811 | 24 | 6.896 | 22.5 | 6.8388 | 25 | 6.8518 | 24.3 | 13.7061 | 27 | 13.7205 | 27.9 | 10.9479 | 31 | 10.9622 | 32.4 | 12.7452 | 36 | 12.7601 | 38.7 | 14.3326 | 43 | 14.3497 | 48.6 | 15.3869 | 54 | 15.4018 | 58.5 | 8.8908 | 65 | 8.908
22.5 | 6.4352 | 25 | 6.45 | 23.4 | 6.3988 | 26 | 6.4163 | 25.2 | 12.96 | 28 | 12.9747 | 28.8 | 10.3389 | 32 | 10.3518 | 33.3 | 11.997 | 37 | 12.0101 | 39.6 | 13.4358 | 44 | 13.4497 | 49.5 | 14.5008 | 55 | 14.5163 | 59.4 | 8.2144 | 66 | 8.2288
23.4 | 6.077 | 26 | 6.091 | 24.3 | 6.0357 | 27 | 6.0497 | 26.1 | 12.2142 | 29 | 12.2288 | 29.7 | 9.7694 | 33 | 9.783 | 34.2 | 11.2488 | 38 | 11.2622 | 40.5 | 12.6603 | 45 | 12.6747 | 50.4 | 13.7335 | 56 | 13.7497 | 60.3 | 7.6477 | 67 | 7.6622
24.3 | 5.7189 | 27 | 5.733 | 25.2 | 5.6725 | 28 | 5.6872 | 27 | 11.5003 | 30 | 11.5163 | 30.6 | 9.2176 | 34 | 9.233 | 35.1 | 10.5524 | 39 | 10.5663 | 41.4 | 11.8847 | 46 | 11.8997 | 51.3 | 13.0456 | 57 | 13.0601 | 61.2 | 7.081 | 68 | 7.0934
25.2 | 5.4148 | 28 | 5.429 | 26.1 | 5.3531 | 29 | 5.3663 | 27.9 | 10.8774 | 31 | 10.8913 | 31.5 | 8.7879 | 35 | 8.8018 | 36 | 9.8974 | 40 | 9.9101 | 42.3 | 11.1893 | 47 | 11.2038 | 52.2 | 12.3578 | 58 | 12.3747 | 62.1 | 6.6203 | 69 | 6.6351
26.1 | 5.1497 | 29 | 5.166 | 27 | 5.0732 | 30 | 5.0872 | 28.8 | 10.2544 | 32 | 10.2684 | 32.4 | 8.358 | 36 | 8.3747 | 36.9 | 9.2425 | 41 | 9.258 | 43.2 | 10.5764 | 48 | 10.5913 | 53.1 | 11.67 | 59 | 11.6851 | 63 | 6.1624 | 70 | 6.1768
27 | 4.8855 | 30 | 4.9 | 27.9 | 4.7935 | 31 | 4.808 | 29.7 | 9.6754 | 33 | 9.6913 | 33.3 | 7.9745 | 37 | 7.9913 | 37.8 | 8.7621 | 42 | 8.7768 | 44.1 | 9.9638 | 49 | 9.9768 | 54 | 11.1547 | 60 | 11.1684 | 63.9 | 5.754 | 71 | 5.7684
27.9 | 4.6694 | 31 | 4.683 | 28.8 | 4.5429 | 32 | 4.558 | 30.6 | 9.2331 | 34 | 9.2497 | 34.2 | 7.646 | 38 | 7.6601 | 38.7 | 8.3083 | 43 | 8.3247 | 45 | 9.3914 | 50 | 9.408 | 54.9 | 10.6563 | 61 | 10.6705 | 64.8 | 5.4263 | 72 | 5.4413
28.8 | 4.4532 | 32 | 4.468 | 29.7 | 4.2958 | 33 | 4.3101 | 31.5 | 8.7909 | 35 | 8.808 | 35.1 | 7.3176 | 39 | 7.333 | 39.6 | 7.8544 | 44 | 7.8684 | 45.9 | 8.9463 | 51 | 8.9601 | 55.8 | 10.1579 | 62 | 10.1747 | 65.7 | 5.0988 | 73 | 5.1163
29.7 | 4.2599 | 33 | 4.275 | 30.6 | 4.1099 | 34 | 4.1247 | 32.4 | 8.3486 | 36 | 8.3622 | 36 | 6.9945 | 40 | 7.008 | 40.5 | 7.488 | 45 | 7.5018 | 46.8 | 8.5011 | 52 | 8.5163 | 56.7 | 9.7396 | 63 | 9.7538 | 66.6 | 4.7712 | 74 | 4.7851
30.6 | 4.0909 | 34 | 4.108 | 31.5 | 3.9442 | 35 | 3.958 | 33.3 | 7.9596 | 37 | 7.9747 | 36.9 | 6.7324 | 41 | 6.7497 | 41.4 | 7.1421 | 46 | 7.158 | 47.7 | 8.0561 | 53 | 8.0705 | 57.6 | 9.3686 | 64 | 9.383 | 67.5 | 4.5133 | 75 | 4.5268
31.5 | 3.9221 | 35 | 3.935 | 32.4 | 3.7783 | 36 | 3.7934 | 34.2 | 7.6229 | 38 | 7.6372 | 37.8 | 6.4703 | 42 | 6.4851 | 42.3 | 6.7963 | 47 | 6.8101 | 48.6 | 7.6986 | 54 | 7.7122 | 58.5 | 8.9815 | 65 | 8.9955 | 68.4 | 4.2615 | 76 | 4.2768
32.4 | 3.7621 | 36 | 3.777 | 33.3 | 3.6313 | 37 | 3.6455 | 35.1 | 7.2862 | 39 | 7.2997 | 38.7 | 6.2082 | 43 | 6.2247 | 43.2 | 6.4671 | 48 | 6.483 | 49.5 | 7.3683 | 55 | 7.383 | 59.4 | 8.2667 | 66 | 8.283 | 69.3 | 4.0097 | 77 | 4.0247
33.3 | 3.6172 | 37 | 3.633 | 34.2 | 3.493 | 38 | 3.508 | 36 | 6.9496 | 40 | 6.9663 | 39.6 | 5.9603 | 44 | 5.9747 | 44.1 | 6.195 | 49 | 6.2101 | 50.4 | 7.0381 | 56 | 7.0518 | 60.3 | 7.636 | 67 | 7.6497 | 70.2 | 3.7685 | 78 | 3.783
34.2 | 3.4723 | 38 | 3.487 | 35.1 | 3.3548 | 39 | 3.3684 | 36.9 | 6.6595 | 41 | 6.6747 | 40.5 | 5.7649 | 45 | 5.7788 | 45 | 5.9229 | 50 | 5.9372 | 51.3 | 6.7078 | 57 | 6.7247 | 61.2 | 7.1285 | 68 | 7.1434 | 71.1 | 3.5991 | 79 | 3.6163
35.1 | 3.3275 | 39 | 3.341 | 36 | 3.2165 | 40 | 3.233 | 37.8 | 6.4334 | 42 | 6.4497 | 41.4 | 5.5694 | 46 | 5.583 | 45.9 | 5.6508 | 51 | 5.6663 | 52.2 | 6.4642 | 58 | 6.4788 | 62.1 | 6.621 | 69 | 6.6351 | 72 | 3.4298 | 80 | 3.4434
36 | 3.2078 | 40 | 3.225 | 36.9 | 3.1069 | 41 | 3.1205 | 38.7 | 6.2074 | 43 | 6.2247 | 42.3 | 5.3741 | 47 | 5.3913 | 46.8 | 5.4373 | 52 | 5.4518 | 53.1 | 6.2277 | 59 | 6.2413 | 63 | 6.1794 | 70 | 6.1934 | 72.9 | 3.2604 | 81 | 3.2747
36.9 | 3.1026 | 41 | 3.116 | 37.8 | 2.9984 | 42 | 3.0122 | 39.6 | 5.9814 | 44 | 5.9955 | 43.2 | 5.1787 | 48 | 5.1934 | 47.7 | 5.2406 | 53 | 5.258 | 54 | 5.9913 | 60 | 6.008 | 63.9 | 5.7549 | 71 | 5.7684 | 73.8 | 3.0911 | 82 | 3.108
37.8 | 2.9974 | 42 | 3.012 | 38.7 | 2.8901 | 43 | 2.9038 | 40.5 | 5.7555 | 45 | 5.7684 | 44.1 | 5.0016 | 49 | 5.0163 | 48.6 | 5.0438 | 54 | 5.058 | 54.9 | 5.7549 | 61 | 5.7684 | 64.8 | 5.3415 | 72 | 5.358 | 74.7 | 2.96 | 83 | 2.9747
38.7 | 2.8924 | 43 | 2.908 | 39.6 | 2.7892 | 44 | 2.8038 | 41.4 | 5.5466 | 46 | 5.5601 | 45 | 4.8561 | 50 | 4.8705 | 49.5 | 4.847 | 55 | 4.8601 | 55.8 | 5.5185 | 62 | 5.533 | 65.7 | 5.0544 | 73 | 5.0684 | 75.6 | 2.8339 | 84 | 2.8497
39.6 | 2.7999 | 44 | 2.816 | 40.5 | 2.7096 | 45 | 2.7247 | 42.3 | 5.3751 | 47 | 5.3913 | 45.9 | 4.7107 | 51 | 4.7247 | 50.4 | 4.6595 | 56 | 4.6747 | 56.7 | 5.3378 | 63 | 5.3518 | 66.6 | 4.7673 | 74 | 4.783 | 76.5 | 2.7079 | 85 | 2.7247
40.5 | 2.718 | 45 | 2.733 | 41.4 | 2.63 | 46 | 2.6434 | 43.2 | 5.2034 | 48 | 5.2184 | 46.8 | 4.5652 | 52 | 4.5788 | 51.3 | 4.5044 | 57 | 4.5184 | 57.6 | 5.1586 | 64 | 5.1747 | 67.5 | 4.4804 | 75 | 4.4934 | 77.4 | 2.5818 | 86 | 2.5955
41.4 | 2.636 | 46 | 2.65 | 42.3 | 2.5504 | 47 | 2.5663 | 44.1 | 5.0319 | 49 | 5.0455 | 47.7 | 4.4199 | 53 | 4.4351 | 52.2 | 4.3494 | 58 | 4.3663 | 58.5 | 4.9794 | 65 | 4.9934 | 68.4 | 4.2552 | 76 | 4.2684 | 78.3 | 2.4654 | 87 | 2.4788
42.3 | 2.5541 | 47 | 2.568 | 43.2 | 2.4708 | 48 | 2.4851 | 45 | 4.8603 | 50 | 4.8747 | 48.6 | 4.2987 | 54 | 4.3122 | 53.1 | 4.1943 | 59 | 4.208 | 59.4 | 4.8002 | 66 | 4.8163 | 69.3 | 4.0462 | 77 | 4.0601 | 79.2 | 2.363 | 88 | 2.3768
43.2 | 2.4781 | 48 | 2.491 | 44.1 | 2.4021 | 49 | 2.4163 | 45.9 | 4.6888 | 51 | 4.7018 | 49.5 | 4.1903 | 55 | 4.2038 | 54 | 4.0477 | 60 | 4.0622 | 60.3 | 4.6506 | 67 | 4.6663 | 70.2 | 3.8372 | 78 | 3.8518 | 80.1 | 2.2605 | 89 | 2.2747
44.1 | 2.4099 | 49 | 2.425 | 45 | 2.3357 | 50 | 2.3497 | 46.8 | 4.5444 | 52 | 4.558 | 50.4 | 4.082 | 56 | 4.0955 | 54.9 | 3.935 | 61 | 3.9497 | 61.2 | 4.5095 | 68 | 4.5247 | 71.1 | 3.6283 | 79 | 3.6434 | 81 | 2.1581 | 90 | 2.1747
45 | 2.3417 | 50 | 2.358 | 45.9 | 2.2694 | 51 | 2.283 | 47.7 | 4.4258 | 53 | 4.4413 | 51.3 | 3.9736 | 57 | 3.9872 | 55.8 | 3.8224 | 62 | 3.8372 | 62.1 | 4.3684 | 69 | 4.383 | 72 | 3.4549 | 80 | 3.4684 | 81.9 | 2.0604 | 91 | 2.0747
45.9 | 2.2735 | 51 | 2.287 | 46.8 | 2.2031 | 52 | 2.2184 | 48.6 | 4.3073 | 54 | 4.3247 | 52.2 | 3.8657 | 58 | 3.883 | 56.7 | 3.7098 | 63 | 3.7247 | 63 | 4.2273 | 70 | 4.2413 | 72.9 | 3.2838 | 81 | 3.2997 | 82.8 | 1.9856 | 92 | 1.9997
46.8 | 2.2053 | 52 | 2.218 | 47.7 | 2.1472 | 53 | 2.1601 | 49.5 | 4.1887 | 55 | 4.2018 | 53.1 | 3.7714 | 59 | 3.7851 | 57.6 | 3.5972 | 64 | 3.6101 | 63.9 | 4.0863 | 71 | 4.0997 | 73.8 | 3.1126 | 82 | 3.1268 | 83.7 | 1.9108 | 93 | 1.9247
47.7 | 2.1493 | 53 | 2.166 | 48.6 | 2.1003 | 54 | 2.1163 | 50.4 | 4.0702 | 56 | 4.0851 | 54 | 3.6772 | 60 | 3.6913 | 58.5 | 3.4845 | 65 | 3.4997 | 64.8 | 3.9732 | 72 | 3.9872 | 74.7 | 2.9664 | 83 | 2.983 | 84.6 | 1.8361 | 94 | 1.8497
48.6 | 2.1012 | 54 | 2.116 | 49.5 | 2.0534 | 55 | 2.0684 | 51.3 | 3.9516 | 57 | 3.9663 | 54.9 | 3.583 | 61 | 3.5997 | 59.4 | 3.3996 | 66 | 3.4163 | 65.7 | 3.8765 | 73 | 3.8913 | 75.6 | 2.8451 | 84 | 2.8601 | 85.5 | 1.7616 | 95 | 1.7768
49.5 | 2.053 | 55 | 2.066 | 50.4 | 2.0065 | 56 | 2.0205 | 52.2 | 3.8568 | 58 | 3.8705 | 55.8 | 3.4887 | 62 | 3.5018 | 60.3 | 3.3185 | 67 | 3.333 | 66.6 | 3.7798 | 74 | 3.7934 | 76.5 | 2.7239 | 85 | 2.7372 | 86.4 | 1.7043 | 96 | 1.7184
50.4 | 2.0048 | 56 | 2.018 | 51.3 | 1.9596 | 57 | 1.9747 | 53.1 | 3.7638 | 59 | 3.7768 | 56.7 | 3.3978 | 63 | 3.4122 | 61.2 | 3.2374 | 68 | 3.2518 | 67.5 | 3.6831 | 75 | 3.6997 | 77.4 | 2.6026 | 86 | 2.6163 | 87.3 | 1.647 | 97 | 1.6601
51.3 | 1.9566 | 57 | 1.971 | 52.2 | 1.9074 | 58 | 1.9247 | 54 | 3.6708 | 60 | 3.6851 | 57.6 | 3.3288 | 64 | 3.3434 | 62.1 | 3.1564 | 69 | 3.1705 | 68.4 | 3.5864 | 76 | 3.5997 | 78.3 | 2.4853 | 87 | 2.4997 | 88.2 | 1.5897 | 98 | 1.6038
52.2 | 1.9068 | 58 | 1.921 | 53.1 | 1.8517 | 59 | 1.8663 | 54.9 | 3.5778 | 61 | 3.5913 | 58.5 | 3.2597 | 65 | 3.2747 | 63 | 3.0753 | 70 | 3.0913 | 69.3 | 3.4897 | 77 | 3.5038 | 79.2 | 2.3783 | 88 | 2.3934 | 89.1 | 1.5325 | 99 | 1.5497
53.1 | 1.8514 | 59 | 1.866 | 54 | 1.7783 | 60 | 1.7934 | 55.8 | 3.4848 | 62 | 3.4997 | 59.4 | 3.1907 | 66 | 3.208 | 63.9 | 2.9943 | 71 | 3.008 | 70.2 | 3.3931 | 78 | 3.408 | 80.1 | 2.2712 | 89 | 2.2851 | 90 | 1.4827 | 100 | 1.4997
54 | 1.7756 | 60 | 1.791 | 54.9 | 1.7049 | 61 | 1.7184 | 56.7 | 3.3919 | 63 | 3.408 | 60.3 | 3.1217 | 67 | 3.1351 | 64.8 | 2.9177 | 72 | 2.933 | 71.1 | 3.2964 | 79 | 3.3101 | 81 | 2.1642 | 90 | 2.1768 | 90.9 | 1.4386 | 101 | 1.4518
54.9 | 1.6998 | 61 | 1.716 | 55.8 | 1.6315 | 62 | 1.6455 | 57.6 | 3.3226 | 64 | 3.3372 | 61.2 | 3.0527 | 68 | 3.0663 | 65.7 | 2.8535 | 73 | 2.8684 | 72 | 3.2258 | 80 | 3.2413 | 81.9 | 2.0608 | 91 | 2.0747 | 91.8 | 1.3944 | 102 | 1.408
55.8 | 1.6239 | 62 | 1.637 | 56.7 | 1.5706 | 63 | 1.5851 | 58.5 | 3.2568 | 65 | 3.2705 | 62.1 | 2.9903 | 69 | 3.0038 | 66.6 | 2.7893 | 74 | 2.8038 | 72.9 | 3.1583 | 81 | 3.1747 | 82.8 | 1.983 | 92 | 1.9997 | 92.7 | 1.3503 | 103 | 1.3663
56.7 | 1.5641 | 63 | 1.577 | 57.6 | 1.5163 | 64 | 1.533 | 59.4 | 3.191 | 66 | 3.208 | 63 | 2.9355 | 70 | 2.9497 | 67.5 | 2.725 | 75 | 2.7413 | 73.8 | 3.0908 | 82 | 3.108 | 83.7 | 1.9053 | 93 | 1.9184 | 93.6 | 1.3062 | 104 | 1.3205
57.6 | 1.5054 | 64 | 1.518 | 58.5 | 1.4621 | 65 | 1.4768 | 60.3 | 3.1251 | 67 | 3.1413 | 63.9 | 2.8807 | 71 | 2.8955 | 68.4 | 2.6608 | 76 | 2.6747 | 74.7 | 2.9813 | 83 | 2.9955 | 84.6 | 1.8276 | 94 | 1.8413 | 94.5 | 1.2622 | 105 | 1.2768
58.5 | 1.4466 | 65 | 1.46 | 59.4 | 1.4079 | 66 | 1.4247 | 61.2 | 3.0593 | 68 | 3.0747 | 64.8 | 2.8259 | 72 | 2.8413 | 69.3 | 2.6033 | 77 | 2.6184 | 75.6 | 2.8545 | 84 | 2.8684 | 85.5 | 1.7626 | 95 | 1.7768 | 95.4 | 1.2299 | 106 | 1.2434
59.4 | 1.3922 | 66 | 1.408 | 60.3 | 1.3536 | 67 | 1.3684 | 62.1 | 2.9935 | 69 | 3.008 | 65.7 | 2.7712 | 73 | 2.7851 | 70.2 | 2.553 | 78 | 2.5663 | 76.5 | 2.7276 | 85 | 2.7413 | 86.4 | 1.7042 | 96 | 1.7184 | 96.3 | 1.1983 | 107 | 1.2122
60.3 | 1.3434 | 67 | 1.358 | 61.2 | 1.3035 | 68 | 1.3184 | 63 | 2.9277 | 70 | 2.9413 | 66.6 | 2.7164 | 74 | 2.733 | 71.1 | 2.5026 | 79 | 2.5163 | 77.4 | 2.6008 | 86 | 2.6163 | 87.3 | 1.6459 | 97 | 1.6601 | 97.2 | 1.1668 | 108 | 1.183
61.2 | 1.2948 | 68 | 1.31 | 62.1 | 1.26 | 69 | 1.2747 | 63.9 | 2.8715 | 71 | 2.8851 | 67.5 | 2.6617 | 75 | 2.6768 | 72 | 2.4523 | 80 | 2.4663 | 78.3 | 2.4837 | 87 | 2.4997 | 88.2 | 1.5876 | 98 | 1.6018 | 98.1 | 1.1353 | 109 | 1.1497
62.1 | 1.2461 | 69 | 1.26 | 63 | 1.2165 | 70 | 1.233 | 64.8 | 2.8174 | 72 | 2.833 | 68.4 | 2.6069 | 76 | 2.6205 | 72.9 | 2.402 | 81 | 2.4163 | 79.2 | 2.3807 | 88 | 2.3934 | 89.1 | 1.5311 | 99 | 1.5455 | 99 | 1.1038 | 110 | 1.1184
63 | 1.1975 | 70 | 1.21 | 63.9 | 1.1731 | 71 | 1.1872 | 65.7 | 2.7633 | 73 | 2.7768 | 69.3 | 2.5581 | 77 | 2.5747 | 73.8 | 2.3516 | 82 | 2.3663 | 80.1 | 2.2777 | 89 | 2.2913 | 90 | 1.4862 | 100 | 1.4997 | 99.9 | 1.0723 | 111 | 1.0851
63.9 | 1.1593 | 71 | 1.175 | 64.8 | 1.1296 | 72 | 1.1434 | 66.6 | 2.7092 | 74 | 2.7247 | 70.2 | 2.5181 | 78 | 2.533 | 74.7 | 2.3174 | 83 | 2.333 | 81 | 2.1748 | 90 | 2.1913 | 90.9 | 1.4413 | 101 | 1.458 | 100.8 | 1.0419 | 112 | 1.058
64.8 | 1.1232 | 72 | 1.137 | 65.7 | 1.0861 | 73 | 1.0997 | 67.5 | 2.6552 | 75 | 2.6684 | 71.1 | 2.4782 | 79 | 2.4934 | 75.6 | 2.2852 | 84 | 2.2997 | 81.9 | 2.0719 | 91 | 2.0851 | 91.8 | 1.3963 | 102 | 1.4101 | 101.7 | 1.0168 | 113 | 1.033
65.7 | 1.087 | 73 | 1.102 | 66.6 | 1.0508 | 74 | 1.0663 | 68.4 | 2.6011 | 76 | 2.6163 | 72 | 2.4383 | 80 | 2.4518 | 76.5 | 2.2531 | 85 | 2.2663 | 82.8 | 1.9956 | 92 | 2.0101 | 92.7 | 1.3514 | 103 | 1.3663 | 102.6 | 0.99158 | 114 | 1.008
66.6 | 1.0509 | 74 | 1.066 | 67.5 | 1.0195 | 75 | 1.033 | 69.3 | 2.5506 | 77 | 2.5663 | 72.9 | 2.3983 | 81 | 2.4122 | 77.4 | 2.2209 | 86 | 2.2351 | 83.7 | 1.9229 | 93 | 1.9372 | 93.6 | 1.3066 | 104 | 1.3205 | 103.5 | 0.9664 | 115 | 0.983
67.5 | 1.0148 | 75 | 1.029 | 68.4 | 0.98808 | 76 | 1.0018 | 70.2 | 2.5075 | 78 | 2.5247 | 73.8 | 2.3584 | 82 | 2.3747 | 78.3 | 2.1888 | 87 | 2.2018 | 84.6 | 1.8501 | 94 | 1.8663 | 94.5 | 1.2617 | 105 | 1.2768 | 104.4 | 0.94123 | 116 | 0.958
68.4 | 0.98226 | 76 | 1 | 69.3 | 0.95671 | 77 | 0.9705 | 71.1 | 2.4644 | 79 | 2.4788 | 74.7 | 2.3184 | 83 | 2.333 | 79.2 | 2.1567 | 88 | 2.1705 | 85.5 | 1.7774 | 95 | 1.7913 | 95.4 | 1.2293 | 106 | 1.2434 | 105.3 | 0.91607 | 117 | 0.933
69.3 | 0.95392 | 77 | 0.968 | 70.2 | 0.92533 | 78 | 0.94134 | 72 | 2.4213 | 80 | 2.4351 | 75.6 | 2.2785 | 84 | 2.2934 | 80.1 | 2.1246 | 89 | 2.1413 | 86.4 | 1.7047 | 96 | 1.7184 | 96.3 | 1.197 | 107 | 1.2101 | 106.2 | 0.89637 | 118 | 0.91009
70.2 | 0.92558 | 78 | 0.941 | 71.1 | 0.89756 | 79 | 0.91217 | 72.9 | 2.3782 | 81 | 2.3934 | 76.5 | 2.2386 | 85 | 2.2518 | 81 | 2.0924 | 90 | 2.108 | 87.3 | 1.6485 | 97 | 1.6622 | 97.2 | 1.1647 | 108 | 1.1788 | 107.1 | 0.8808 | 119 | 0.89342
71.1 | 0.89727 | 79 | 0.91 | 72 | 0.87271 | 80 | 0.88717 | 73.8 | 2.3352 | 82 | 2.3497 | 77.4 | 2.2038 | 86 | 2.2184 | 81.9 | 2.0468 | 91 | 2.0601 | 88.2 | 1.5935 | 98 | 1.608 | 98.1 | 1.1324 | 109 | 1.1497 | 108 | 0.86523 | 120 | 0.87884
72 | 0.86894 | 80 | 0.883 | 72.9 | 0.84785 | 81 | 0.86217 | 74.7 | 2.2921 | 83 | 2.308 | 78.3 | 2.1747 | 87 | 2.1913 | 82.8 | 1.9766 | 92 | 1.9913 | 89.1 | 1.5386 | 99 | 1.5518 | 99 | 1.1001 | 110 | 1.1163 | 108.9 | 0.84967 | 121 | 0.86634
72.9 | 0.84612 | 81 | 0.86 | 73.8 | 0.82299 | 82 | 0.83717 | 75.6 | 2.2618 | 84 | 2.2768 | 79.2 | 2.1455 | 88 | 2.1601 | 83.7 | 1.9064 | 93 | 1.9205 | 90 | 1.4837 | 100 | 1.4997 | 99.9 | 1.0678 | 111 | 1.083 | 109.8 | 0.8341 | 122 | 0.84967
73.8 | 0.82422 | 82 | 0.841 | 74.7 | 0.79818 | 83 | 0.81217 | 76.5 | 2.2325 | 85 | 2.2497 | 80.1 | 2.1164 | 89 | 2.133 | 84.6 | 1.8362 | 94 | 1.8497 | 90.9 | 1.4288 | 101 | 1.4434 | 100.8 | 1.0384 | 112 | 1.0518 | 110.7 | 0.81857 | 123 | 0.833
74.7 | 0.80237 | 83 | 0.816 | 75.6 | 0.77464 | 84 | 0.79134 | 77.4 | 2.2031 | 86 | 2.2163 | 81 | 2.0872 | 90 | 2.1018 | 85.5 | 1.7712 | 95 | 1.7851 | 91.8 | 1.3878 | 102 | 1.4018 | 101.7 | 1.0143 | 113 | 1.0288 | 111.6 | 0.80303 | 124 | 0.81842
75.6 | 0.78049 | 84 | 0.793 | 76.5 | 0.75521 | 85 | 0.76842 | 78.3 | 2.1737 | 87 | 2.1872 | 81.9 | 2.0581 | 91 | 2.0747 | 86.4 | 1.7135 | 96 | 1.7268 | 92.7 | 1.3502 | 103 | 1.3663 | 102.6 | 0.99012 | 114 | 1.0038 | 112.5 | 0.78747 | 125 | 0.80175
76.5 | 0.75864 | 85 | 0.775 | 77.4 | 0.73577 | 86 | 0.74967 | 79.2 | 2.1443 | 88 | 2.158 | 82.8 | 1.9823 | 92 | 1.9997 | 87.3 | 1.6559 | 97 | 1.6684 | 93.6 | 1.3126 | 104 | 1.3268 | 103.5 | 0.96596 | 115 | 0.983 | 113.4 | 0.77195 | 126 | 0.78509
77.4 | 0.73677 | 86 | 0.752 | 78.3 | 0.71632 | 87 | 0.733 | 80.1 | 2.115 | 89 | 2.1288 | 83.7 | 1.9054 | 93 | 1.9184 | 88.2 | 1.5982 | 98 | 1.6122 | 94.5 | 1.2751 | 105 | 1.2913 | 104.4 | 0.94182 | 116 | 0.958 | 114.3 | 0.75854 | 127 | 0.77467
78.3 | 0.71492 | 87 | 0.729 | 79.2 | 0.69692 | 88 | 0.71009 | 81 | 2.0856 | 90 | 2.0997 | 84.6 | 1.8286 | 94 | 1.8434 | 89.1 | 1.5405 | 99 | 1.5538 | 95.4 | 1.2375 | 106 | 1.2518 | 105.3 | 0.91768 | 117 | 0.933 | 115.2 | 0.74672 | 128 | 0.76009
79.2 | 0.69613 | 88 | 0.71 | 80.1 | 0.6775 | 89 | 0.69134 | 81.9 | 2.0297 | 91 | 2.0434 | 85.5 | 1.754 | 95 | 1.7684 | 90 | 1.4883 | 100 | 1.5018 | 96.3 | 1.2 | 107 | 1.2163 | 106.2 | 0.89556 | 118 | 0.91009 | 116.1 | 0.7349 | 129 | 0.74967
80.1 | 0.67985 | 89 | 0.693 | 81 | 0.65809 | 90 | 0.67467 | 82.8 | 1.964 | 92 | 1.9768 | 86.4 | 1.697 | 96 | 1.7101 | 90.9 | 1.4455 | 101 | 1.4601 | 97.2 | 1.1624 | 108 | 1.1768 | 107.1 | 0.87901 | 119 | 0.89342 | 117 | 0.72309 | 130 | 0.73717
81 | 0.66357 | 90 | 0.677 | 81.9 | 0.64239 | 91 | 0.658 | 83.7 | 1.8984 | 93 | 1.9122 | 87.3 | 1.6401 | 97 | 1.6538 | 91.8 | 1.4027 | 102 | 1.4163 | 98.1 | 1.1249 | 109 | 1.1413 | 108 | 0.86245 | 120 | 0.87675 | 117.9 | 0.71127 | 131 | 0.72467
81.9 | 0.64732 | 91 | 0.66 | 82.8 | 0.6274 | 92 | 0.64134 | 84.6 | 1.8332 | 94 | 1.8497 | 88.2 | 1.5831 | 98 | 1.5997 | 92.7 | 1.3599 | 103 | 1.3747 | 99 | 1.0964 | 110 | 1.1101 | 108.9 | 0.84589 | 121 | 0.86009 | 118.8 | 0.69947 | 132 | 0.71634
82.8 | 0.63104 | 92 | 0.646 | 83.7 | 0.61243 | 93 | 0.62675 | 85.5 | 1.7697 | 95 | 1.783 | 89.1 | 1.5262 | 99 | 1.5413 | 93.6 | 1.3172 | 104 | 1.333 | 99.9 | 1.0698 | 111 | 1.0851 | 109.8 | 0.82935 | 122 | 0.84342 | 119.7 | 0.68765 | 133 | 0.70175
83.7 | 0.61478 | 93 | 0.629 | 84.6 | 0.5975 | 94 | 0.61217 | 86.4 | 1.7061 | 96 | 1.7205 | 90 | 1.4795 | 100 | 1.4934 | 94.5 | 1.2744 | 105 | 1.2913 | 100.8 | 1.0432 | 112 | 1.058 | 110.7 | 0.81282 | 123 | 0.82675 | 120.6 | 0.67584 | 134 | 0.69134
84.6 | 0.59854 | 94 | 0.612 | 85.5 | 0.58254 | 95 | 0.59967 | 87.3 | 1.6427 | 97 | 1.658 | 90.9 | 1.4376 | 101 | 1.4518 | 95.4 | 1.2409 | 106 | 1.258 | 101.7 | 1.0167 | 113 | 1.033 | 111.6 | 0.7963 | 124 | 0.81009 | 121.5 | 0.66404 | 135 | 0.67675
85.5 | 0.58228 | 95 | 0.6 | 86.4 | 0.56758 | 96 | 0.583 | 88.2 | 1.5791 | 98 | 1.5934 | 91.8 | 1.3958 | 102 | 1.4101 | 96.3 | 1.2081 | 107 | 1.2247 | 102.6 | 0.99016 | 114 | 1.0038 | 112.5 | 0.782 | 125 | 0.7955 | 122.4 | 0.65225 | 136 | 0.66634
86.4 | 0.56818 | 96 | 0.583 | 87.3 | 0.55264 | 97 | 0.56634 | 89.1 | 1.5157 | 99 | 1.5288 | 92.7 | 1.354 | 103 | 1.3684 | 97.2 | 1.1752 | 108 | 1.1913 | 103.5 | 0.9636 | 115 | 0.97675 | 113.4 | 0.77028 | 126 | 0.78509 | 123.3 | 0.64046 | 137 | 0.65384
87.3 | 0.5557 | 97 | 0.568 | 88.2 | 0.53771 | 98 | 0.55175 | 90 | 1.4744 | 100 | 1.4913 | 93.6 | 1.3122 | 104 | 1.3268 | 98.1 | 1.1424 | 109 | 1.158 | 104.4 | 0.93706 | 116 | 0.95175 | 114.3 | 0.75856 | 127 | 0.77467 | 124.2 | 0.62868 | 138 | 0.64342
88.2 | 0.54322 | 98 | 0.558 | 89.1 | 0.52643 | 99 | 0.54134 | 90.9 | 1.4335 | 101 | 1.4497 | 94.5 | 1.2705 | 105 | 1.2851 | 99 | 1.1095 | 110 | 1.1247 | 105.3 | 0.91803 | 117 | 0.933 | 115.2 | 0.74685 | 128 | 0.76009 | 125.1 | 0.61896 | 139 | 0.633
89.1 | 0.53075 | 99 | 0.546 | 90 | 0.51605 | 100 | 0.533 | 91.8 | 1.3927 | 102 | 1.408 | 95.4 | 1.2305 | 106 | 1.2434 | 99.9 | 1.0767 | 111 | 1.0913 | 106.2 | 0.89971 | 118 | 0.91634 | 116.1 | 0.73514 | 129 | 0.74967 | 126 | 0.60994 | 140 | 0.62467
90 | 0.51828 | 100 | 0.533 | 90.9 | 0.50568 | 101 | 0.5205 | 92.7 | 1.3518 | 103 | 1.3663 | 96.3 | 1.1993 | 107 | 1.2163 | 100.8 | 1.0438 | 112 | 1.058 | 107.1 | 0.88139 | 119 | 0.8955 | 117 | 0.72344 | 130 | 0.73717 | 126.9 | 0.60097 | 141 | 0.61634
90.9 | 0.50581 | 101 | 0.521 | 91.8 | 0.49529 | 102 | 0.51009 | 93.6 | 1.311 | 104 | 1.3247 | 97.2 | 1.1681 | 108 | 1.183 | 101.7 | 1.0168 | 113 | 1.033 | 108 | 0.86307 | 120 | 0.87675 | 117.9 | 0.71173 | 131 | 0.72675 | 127.8 | 0.59196 | 142 | 0.608
91.8 | 0.49335 | 102 | 0.508 | 92.7 | 0.48493 | 103 | 0.49967 | 94.5 | 1.2701 | 105 | 1.2851 | 98.1 | 1.1369 | 109 | 1.1518 | 102.6 | 0.99372 | 114 | 1.008 | 108.9 | 0.84476 | 121 | 0.86009 | 118.8 | 0.70002 | 132 | 0.71634 | 128.7 | 0.58299 | 143 | 0.59967
92.7 | 0.48376 | 103 | 0.5 | 93.6 | 0.47459 | 104 | 0.49134 | 95.4 | 1.2348 | 106 | 1.2497 | 99 | 1.1056 | 110 | 1.1184 | 103.5 | 0.97061 | 115 | 0.98509 | 109.8 | 0.82645 | 122 | 0.84134 | 119.7 | 0.68833 | 133 | 0.70175 | 129.6 | 0.57399 | 144 | 0.59134
93.6 | 0.47419 | 104 | 0.491 | 94.5 | 0.46424 | 105 | 0.47884 | 96.3 | 1.1999 | 107 | 1.2163 | 99.9 | 1.0744 | 111 | 1.0913 | 104.4 | 0.94751 | 116 | 0.96009 | 110.7 | 0.80932 | 123 | 0.82467 | 120.6 | 0.67663 | 134 | 0.69134 | 130.5 | 0.565 | 145 | 0.57884
94.5 | 0.4646 | 105 | 0.479 | 95.4 | 0.45391 | 106 | 0.46842 | 97.2 | 1.1649 | 108 | 1.1788 | 100.8 | 1.0436 | 112 | 1.058 | 105.3 | 0.92441 | 117 | 0.94134 | 111.6 | 0.79644 | 124 | 0.81009 | 121.5 | 0.66495 | 135 | 0.67884 | 131.4 | 0.556 | 146 | 0.5705
95.4 | 0.45503 | 106 | 0.468 | 96.3 | 0.44358 | 107 | 0.458 | 98.1 | 1.13 | 109 | 1.1434 | 101.7 | 1.0181 | 113 | 1.033 | 106.2 | 0.90131 | 118 | 0.91634 | 112.5 | 0.78355 | 125 | 0.79967 | 122.4 | 0.65326 | 136 | 0.66842 | 132.3 | 0.54704 | 147 | 0.56009
96.3 | 0.44546 | 107 | 0.46 | 97.2 | 0.43325 | 108 | 0.44967 | 99 | 1.0951 | 110 | 1.1101 | 102.6 | 0.99264 | 114 | 1.008 | 107.1 | 0.87822 | 119 | 0.89342 | 113.4 | 0.77068 | 126 | 0.78509 | 123.3 | 0.64158 | 137 | 0.658 | 133.2 | 0.53805 | 148 | 0.55175
97.2 | 0.43588 | 108 | 0.45 | 98.1 | 0.42417 | 109 | 0.44134 | 99.9 | 1.0658 | 111 | 1.083 | 103.5 | 0.96716 | 115 | 0.983 | 108 | 0.8634 | 120 | 0.87675 | 114.3 | 0.7578 | 127 | 0.77467 | 124.2 | 0.62991 | 138 | 0.64342 | 134.1 | 0.52908 | 149 | 0.54342
98.1 | 0.42632 | 109 | 0.441 | 99 | 0.41634 | 110 | 0.433 | 100.8 | 1.0409 | 112 | 1.058 | 104.4 | 0.94169 | 116 | 0.958 | 108.9 | 0.84878 | 121 | 0.86634 | 115.2 | 0.74494 | 128 | 0.76009 | 125.1 | 0.62027 | 139 | 0.63509 | 135 | 0.52012 | 150 | 0.53509
99 | 0.41676 | 110 | 0.433 | 99.9 | 0.4085 | 111 | 0.42467 | 101.7 | 1.0159 | 113 | 1.033 | 105.3 | 0.91623 | 117 | 0.933 | 109.8 | 0.83414 | 122 | 0.84967 | 116.1 | 0.73206 | 129 | 0.74967 | 126 | 0.61106 | 140 | 0.62467 | 135.9 | 0.51303 | 151 | 0.52675
99.9 | 0.40809 | 111 | 0.425 | 100.8 | 0.40068 | 112 | 0.41634 | 102.6 | 0.99099 | 114 | 1.008 | 106.2 | 0.89497 | 118 | 0.91009 | 110.7 | 0.81955 | 123 | 0.833 | 117 | 0.7192 | 130 | 0.733 | 126.9 | 0.6019 | 141 | 0.61634 | 136.8 | 0.50657 | 152 | 0.5205
100.8 | 0.40076 | 112 | 0.416 | 101.7 | 0.39288 | 113 | 0.408 | 103.5 | 0.96604 | 115 | 0.983 | 107.1 | 0.87869 | 119 | 0.89342 | 111.6 | 0.80494 | 124 | 0.81842 | 117.9 | 0.70634 | 131 | 0.7205 | 127.8 | 0.5927 | 142 | 0.608 | 137.7 | 0.50011 | 153 | 0.51634
101.7 | 0.39346 | 113 | 0.408 | 102.6 | 0.38504 | 114 | 0.39967 | 104.4 | 0.94109 | 116 | 0.958 | 108 | 0.86243 | 120 | 0.87675 | 112.5 | 0.79032 | 125 | 0.80384 | 118.8 | 0.6935 | 132 | 0.708 | 128.7 | 0.58355 | 143 | 0.59967 | 138.6 | 0.49365 | 154 | 0.508
102.6 | 0.38613 | 114 | 0.4 | 103.5 | 0.37721 | 115 | 0.39134 | 105.3 | 0.91616 | 117 | 0.933 | 108.9 | 0.84616 | 121 | 0.86009 | 113.4 | 0.7757 | 126 | 0.79134 | 119.7 | 0.68066 | 133 | 0.69342 | 129.6 | 0.57436 | 144 | 0.59134 | 139.5 | 0.48718 | 155 | 0.50175
103.5 | 0.3788 | 115 | 0.393 | 104.4 | 0.3694 | 116 | 0.383 | 106.2 | 0.89567 | 118 | 0.91009 | 109.8 | 0.8299 | 122 | 0.84342 | 114.3 | 0.76111 | 127 | 0.77467 | 120.6 | 0.6696 | 134 | 0.683 | 130.5 | 0.56518 | 145 | 0.57884 | 140.4 | 0.48071 | 156 | 0.49342
104.4 | 0.37148 | 116 | 0.385 | 105.3 | 0.36173 | 117 | 0.37675 | 107.1 | 0.87848 | 119 | 0.89342 | 110.7 | 0.81367 | 123 | 0.82675 | 115.2 | 0.74652 | 128 | 0.76009 | 121.5 | 0.65994 | 135 | 0.67467 | 131.4 | 0.55599 | 146 | 0.5705 | 141.3 | 0.47427 | 157 | 0.49134
105.3 | 0.36416 | 117 | 0.379 | 106.2 | 0.35592 | 118 | 0.3705 | 108 | 0.86131 | 120 | 0.87467 | 111.6 | 0.79743 | 124 | 0.81009 | 116.1 | 0.73194 | 129 | 0.7455 | 122.4 | 0.65029 | 136 | 0.66634 | 132.3 | 0.54684 | 147 | 0.56009 | 142.2 | 0.46782 | 158 | 0.483
106.2 | 0.35685 | 118 | 0.371 | 107.1 | 0.35011 | 119 | 0.36634 | 108.9 | 0.84412 | 121 | 0.858 | 112.5 | 0.78118 | 125 | 0.7955 | 117 | 0.72023 | 130 | 0.73509 | 123.3 | 0.64063 | 137 | 0.658 | 133.2 | 0.53767 | 148 | 0.55175 | 143.1 | 0.46137 | 159 | 0.47467
107.1 | 0.34955 | 119 | 0.366 | 108 | 0.34431 | 120 | 0.358 | 109.8 | 0.82694 | 122 | 0.84134 | 113.4 | 0.76815 | 126 | 0.783 | 117.9 | 0.70927 | 131 | 0.72467 | 124.2 | 0.63099 | 138 | 0.6455 | 134.1 | 0.52852 | 149 | 0.54342 | 144 | 0.4549 | 160 | 0.46842
108 | 0.34224 | 120 | 0.358 | 108.9 | 0.3385 | 121 | 0.35175 | 110.7 | 0.80979 | 123 | 0.82467 | 114.3 | 0.75613 | 127 | 0.7705 | 118.8 | 0.69833 | 132 | 0.71217 | 125.1 | 0.62132 | 139 | 0.63509 | 135 | 0.52058 | 150 | 0.53509 | 144.9 | 0.44846 | 161 | 0.46217
108.9 | 0.33533 | 121 | 0.35 | 109.8 | 0.33268 | 122 | 0.34967 | 111.6 | 0.7953 | 124 | 0.81009 | 115.2 | 0.74412 | 128 | 0.758 | 119.7 | 0.68738 | 133 | 0.70175 | 126 | 0.61166 | 140 | 0.62675 | 135.9 | 0.51407 | 151 | 0.52675 | 145.8 | 0.44202 | 162 | 0.458
109.8 | 0.33027 | 122 | 0.343 | 110.7 | 0.32691 | 123 | 0.34134 | 112.5 | 0.78283 | 125 | 0.79967 | 116.1 | 0.73209 | 129 | 0.74967 | 120.6 | 0.67642 | 134 | 0.69134 | 126.9 | 0.60204 | 141 | 0.61634 | 136.8 | 0.50755 | 152 | 0.52467 | 146.7 | 0.43558 | 163 | 0.44967
110.7 | 0.32522 | 123 | 0.341 | 111.6 | 0.32111 | 124 | 0.33509 | 113.4 | 0.77038 | 126 | 0.78509 | 117 | 0.72009 | 130 | 0.73509 | 121.5 | 0.66548 | 135 | 0.683 | 127.8 | 0.59238 | 142 | 0.608 | 137.7 | 0.50103 | 153 | 0.51634 | 147.6 | 0.42975 | 164 | 0.44342
111.6 | 0.32017 | 124 | 0.335 | 112.5 | 0.31532 | 125 | 0.32884 | 114.3 | 0.75794 | 127 | 0.77467 | 117.9 | 0.70808 | 131 | 0.72467 | 122.4 | 0.65453 | 136 | 0.66842 | 128.7 | 0.58276 | 143 | 0.59967 | 138.6 | 0.49453 | 154 | 0.508 | 148.5 | 0.42445 | 165 | 0.44134
112.5 | 0.31509 | 125 | 0.329 | 113.4 | 0.30953 | 126 | 0.32467 | 115.2 | 0.7455 | 128 | 0.76009 | 118.8 | 0.69608 | 132 | 0.71009 | 123.3 | 0.6436 | 137 | 0.658 | 129.6 | 0.57312 | 144 | 0.58717 | 139.5 | 0.48801 | 155 | 0.50175 | 149.4 | 0.41914 | 166 | 0.433
113.4 | 0.31003 | 126 | 0.325 | 114.3 | 0.30384 | 127 | 0.31842 | 116.1 | 0.73306 | 129 | 0.74967 | 119.7 | 0.68408 | 133 | 0.69967 | 124.2 | 0.63267 | 138 | 0.64967 | 130.5 | 0.56349 | 145 | 0.57675 | 140.4 | 0.48148 | 156 | 0.4955 | 150.3 | 0.41383 | 167 | 0.42675
114.3 | 0.30496 | 127 | 0.318 | 115.2 | 0.29958 | 128 | 0.31634 | 117 | 0.72063 | 130 | 0.73509 | 120.6 | 0.67207 | 134 | 0.68509 | 125.1 | 0.62173 | 139 | 0.63509 | 131.4 | 0.55385 | 146 | 0.56842 | 141.3 | 0.47498 | 157 | 0.49134 | 151.2 | 0.40851 | 168 | 0.42467
115.2 | 0.29991 | 128 | 0.316 | 116.1 | 0.29531 | 129 | 0.31009 | 117.9 | 0.70819 | 131 | 0.72467 | 121.5 | 0.66009 | 135 | 0.67467 | 126 | 0.61079 | 140 | 0.62467 | 132.3 | 0.5443 | 147 | 0.558 | 142.2 | 0.46849 | 158 | 0.483 | 152.1 | 0.40318 | 169 | 0.41842
116.1 | 0.29485 | 129 | 0.31 | 117 | 0.29106 | 130 | 0.308 | 118.8 | 0.69578 | 132 | 0.71009 | 122.4 | 0.6497 | 136 | 0.66634 | 126.9 | 0.59988 | 141 | 0.61634 | 133.2 | 0.53749 | 148 | 0.55175 | 143.1 | 0.46199 | 159 | 0.47675 | 153 | 0.39788 | 170 | 0.41217
117 | 0.28982 | 130 | 0.304 | 117.9 | 0.28679 | 131 | 0.30175 | 119.7 | 0.68336 | 133 | 0.69967 | 123.3 | 0.63985 | 137 | 0.65384 | 127.8 | 0.59 | 142 | 0.60384 | 134.1 | 0.53069 | 149 | 0.5455 | 144 | 0.45549 | 160 | 0.46842 | 153.9 | 0.39255 | 171 | 0.408
117.9 | 0.28478 | 131 | 0.3 | 118.8 | 0.28255 | 132 | 0.29967 | 120.6 | 0.67093 | 134 | 0.68509 | 124.2 | 0.63002 | 138 | 0.64342 | 128.7 | 0.58167 | 143 | 0.5955 | 135 | 0.52389 | 150 | 0.54134 | 144.9 | 0.449 | 161 | 0.46634 | 154.8 | 0.38724 | 172 | 0.40175
118.8 | 0.28063 | 132 | 0.293 | 119.7 | 0.27829 | 133 | 0.29342 | 121.5 | 0.65858 | 135 | 0.67467 | 125.1 | 0.62017 | 139 | 0.63509 | 129.6 | 0.57332 | 144 | 0.58717 | 135.9 | 0.51708 | 151 | 0.533 | 145.8 | 0.44287 | 162 | 0.458 | 155.7 | 0.38192 | 173 | 0.3955
119.7 | 0.27665 | 133 | 0.291 | 120.6 | 0.27402 | 134 | 0.29134 | 122.4 | 0.64879 | 136 | 0.66634 | 126 | 0.6103 | 140 | 0.62467 | 130.5 | 0.56498 | 145 | 0.57884 | 136.8 | 0.51029 | 152 | 0.52467 | 146.7 | 0.4375 | 163 | 0.45175 | 156.6 | 0.37661 | 174 | 0.39134
120.6 | 0.27266 | 134 | 0.287 | 121.5 | 0.26977 | 135 | 0.28509 | 123.3 | 0.639 | 137 | 0.65175 | 126.9 | 0.60049 | 141 | 0.61634 | 131.4 | 0.55662 | 146 | 0.5705 | 137.7 | 0.50348 | 153 | 0.51842 | 147.6 | 0.43211 | 164 | 0.4455 | 157.5 | 0.37131 | 175 | 0.38509
121.5 | 0.26867 | 135 | 0.283 | 122.4 | 0.26553 | 136 | 0.27884 | 124.2 | 0.62921 | 138 | 0.64342 | 127.8 | 0.59064 | 142 | 0.608 | 132.3 | 0.5483 | 147 | 0.56217 | 138.6 | 0.49669 | 154 | 0.51009 | 148.5 | 0.42674 | 165 | 0.44134 | 158.4 | 0.36601 | 176 | 0.383
122.4 | 0.26469 | 136 | 0.279 | 123.3 | 0.26129 | 137 | 0.27467 | 125.1 | 0.6194 | 139 | 0.633 | 128.7 | 0.58081 | 143 | 0.5955 | 133.2 | 0.53995 | 148 | 0.55384 | 139.5 | 0.48989 | 155 | 0.50384 | 149.4 | 0.42137 | 166 | 0.43509 | 159.3 | 0.36072 | 177 | 0.37467
123.3 | 0.26071 | 137 | 0.275 | 124.2 | 0.25706 | 138 | 0.2705 | 126 | 0.6096 | 140 | 0.62467 | 129.6 | 0.57097 | 144 | 0.58509 | 134.1 | 0.53161 | 149 | 0.5455 | 140.4 | 0.48308 | 156 | 0.49967 | 150.3 | 0.41601 | 167 | 0.433 | 160.2 | 0.35705 | 178 | 0.3705
124.2 | 0.25675 | 138 | 0.271 | 125.1 | 0.25281 | 139 | 0.26634 | 126.9 | 0.59983 | 141 | 0.61634 | 130.5 | 0.56116 | 145 | 0.57467 | 135 | 0.52328 | 150 | 0.53717 | 141.3 | 0.4763 | 157 | 0.49134 | 151.2 | 0.41064 | 168 | 0.42467 | 161.1 | 0.35352 | 179 | 0.36842
125.1 | 0.25277 | 139 | 0.266 | 126 | 0.24857 | 140 | 0.26217 | 127.8 | 0.59003 | 142 | 0.60384 | 131.4 | 0.55352 | 146 | 0.56842 | 135.9 | 0.51495 | 151 | 0.52884 | 142.2 | 0.46953 | 158 | 0.483 | 152.1 | 0.40525 | 169 | 0.41842 | 162 | 0.35 | 180 | 0.36634
126 | 0.24878 | 140 | 0.262 | 126.9 | 0.24485 | 141 | 0.26009 | 128.7 | 0.58027 | 143 | 0.59342 | 132.3 | 0.54631 | 147 | 0.56009 | 136.8 | 0.50832 | 152 | 0.52467 | 143.1 | 0.46275 | 159 | 0.47675 | 153 | 0.39989 | 170 | 0.41634 | 162.9 | 0.34646 | 181 | 0.36009
126.9 | 0.24483 | 141 | 0.26 | 127.8 | 0.24167 | 142 | 0.258 | 129.6 | 0.57047 | 144 | 0.58509 | 133.2 | 0.53908 | 148 | 0.55384 | 137.7 | 0.50172 | 153 | 0.51634 | 144 | 0.45596 | 160 | 0.4705 | 153.9 | 0.39451 | 171 | 0.408 | 163.8 | 0.34296 | 182 | 0.358
127.8 | 0.24085 | 142 | 0.258 | 128.7 | 0.23854 | 143 | 0.25175 | 130.5 | 0.56071 | 145 | 0.57467 | 134.1 | 0.53187 | 149 | 0.5455 | 138.6 | 0.49513 | 154 | 0.51009 | 144.9 | 0.44918 | 161 | 0.46634 | 154.8 | 0.38914 | 172 | 0.40175 | 164.7 | 0.33943 | 183 | 0.35384
128.7 | 0.23692 | 143 | 0.252 | 129.6 | 0.23538 | 144 | 0.24967 | 131.4 | 0.55092 | 146 | 0.56634 | 135 | 0.52467 | 150 | 0.54134 | 139.5 | 0.48853 | 155 | 0.50175 | 145.8 | 0.4424 | 162 | 0.458 | 155.7 | 0.38378 | 173 | 0.39967 | 165.6 | 0.3359 | 184 | 0.34967
129.6 | 0.23339 | 144 | 0.25 | 130.5 | 0.23224 | 145 | 0.2455 | 132.3 | 0.54211 | 147 | 0.558 | 135.9 | 0.51745 | 151 | 0.533 | 140.4 | 0.48193 | 156 | 0.4955 | 146.7 | 0.43622 | 163 | 0.44967 | 156.6 | 0.3784 | 174 | 0.39342 | 166.5 | 0.33238 | 185 | 0.34967
130.5 | 0.23047 | 145 | 0.243 | 131.4 | 0.22907 | 146 | 0.24342 | 133.2 | 0.53529 | 148 | 0.54967 | 136.8 | 0.51023 | 152 | 0.52467 | 141.3 | 0.47535 | 157 | 0.49134 | 147.6 | 0.43082 | 164 | 0.4455 | 157.5 | 0.37305 | 175 | 0.38717 | 167.4 | 0.32886 | 186 | 0.34342
131.4 | 0.22751 | 146 | 0.241 | 132.3 | 0.22595 | 147 | 0.24134 | 134.1 | 0.52849 | 149 | 0.54342 | 137.7 | 0.50302 | 153 | 0.51634 | 142.2 | 0.46877 | 158 | 0.483 | 148.5 | 0.42544 | 165 | 0.44134 | 158.4 | 0.36788 | 176 | 0.383 | 168.3 | 0.32532 | 187 | 0.34134
132.3 | 0.22461 | 147 | 0.241 | 133.2 | 0.22279 | 148 | 0.23717 | 135 | 0.52168 | 150 | 0.53509 | 138.6 | 0.49582 | 154 | 0.51009 | 143.1 | 0.46218 | 159 | 0.47675 | 149.4 | 0.42006 | 166 | 0.43509 | 159.3 | 0.364 | 177 | 0.37675 | 169.2 | 0.32182 | 188 | 0.33509
133.2 | 0.22167 | 148 | 0.235 | 134.1 | 0.21966 | 149 | 0.233 | 135.9 | 0.51488 | 151 | 0.52884 | 139.5 | 0.48861 | 155 | 0.50175 | 144 | 0.45559 | 160 | 0.46842 | 150.3 | 0.41467 | 167 | 0.42884 | 160.2 | 0.36012 | 178 | 0.37467 | 170.1 | 0.31831 | 189 | 0.333
134.1 | 0.21874 | 149 | 0.233 | 135 | 0.21653 | 150 | 0.233 | 136.8 | 0.50807 | 152 | 0.52467 | 140.4 | 0.4814 | 156 | 0.4955 | 144.9 | 0.449 | 161 | 0.46634 | 151.2 | 0.40929 | 168 | 0.42467 | 161.1 | 0.35622 | 179 | 0.3705 | 171 | 0.31479 | 190 | 0.32884
135 | 0.21582 | 150 | 0.233 | 135.9 | 0.2134 | 151 | 0.22675 | 137.7 | 0.50126 | 153 | 0.51634 | 141.3 | 0.4742 | 157 | 0.49134 | 145.8 | 0.44242 | 162 | 0.458 | 152.1 | 0.40389 | 169 | 0.41842 | 162 | 0.35235 | 180 | 0.36634 | 171.9 | 0.31129 | 191 | 0.32467
135.9 | 0.2129 | 151 | 0.227 | 136.8 | 0.21026 | 152 | 0.22467 | 138.6 | 0.49447 | 154 | 0.508 | 142.2 | 0.46703 | 158 | 0.483 | 146.7 | 0.43667 | 163 | 0.45175 | 153 | 0.39851 | 170 | 0.41217 | 162.9 | 0.34845 | 181 | 0.36217 | 172.8 | 0.30779 | 192 | 0.32467
136.8 | 0.20997 | 152 | 0.225 | 137.7 | 0.20714 | 153 | 0.2205 | 139.5 | 0.48766 | 155 | 0.50175 | 143.1 | 0.45983 | 159 | 0.47467 | 147.6 | 0.43149 | 164 | 0.4455 | 153.9 | 0.39312 | 171 | 0.408 | 163.8 | 0.34459 | 182 | 0.358 | 173.7 | 0.30428 | 193 | 0.31842
137.7 | 0.20706 | 153 | 0.221 | 138.6 | 0.20402 | 154 | 0.21842 | 140.4 | 0.48086 | 156 | 0.4955 | 144 | 0.45264 | 160 | 0.46634 | 148.5 | 0.42632 | 165 | 0.44134 | 154.8 | 0.38772 | 172 | 0.40175 | 164.7 | 0.34071 | 183 | 0.358 | 174.6 | 0.30078 | 194 | 0.31634
138.6 | 0.20415 | 154 | 0.218 | 139.5 | 0.20089 | 155 | 0.21634 | 141.3 | 0.47407 | 157 | 0.49134 | 144.9 | 0.44711 | 161 | 0.46009 | 149.4 | 0.42116 | 166 | 0.43509 | 155.7 | 0.38235 | 173 | 0.3955 | 165.6 | 0.33682 | 184 | 0.35175 | 175.5 | 0.29728 | 195 | 0.31009
139.5 | 0.20124 | 155 | 0.216 | 140.4 | 0.19776 | 156 | 0.21217 | 142.2 | 0.4673 | 158 | 0.483 | 145.8 | 0.44168 | 162 | 0.458 | 150.3 | 0.41599 | 167 | 0.433 | 156.6 | 0.37695 | 174 | 0.39134 | 166.5 | 0.33294 | 185 | 0.34967 | 176.4 | 0.29377 | 196 | 0.308
140.4 | 0.19832 | 156 | 0.212 | 141.3 | 0.1953 | 157 | 0.21009 | 143.1 | 0.46051 | 159 | 0.47467 | 146.7 | 0.43625 | 163 | 0.44967 | 151.2 | 0.41082 | 168 | 0.42467 | 157.5 | 0.37158 | 175 | 0.38509 | 167.4 | 0.32906 | 186 | 0.34342 | 177.3 | 0.29029 | 197 | 0.30384
141.3 | 0.1956 | 157 | 0.21 | 142.2 | 0.1926 | 158 | 0.208 | 144 | 0.45472 | 160 | 0.46842 | 147.6 | 0.43082 | 164 | 0.4455 | 152.1 | 0.40564 | 169 | 0.41842 | 158.4 | 0.36708 | 176 | 0.383 | 168.3 | 0.32517 | 187 | 0.34134 | 178.2 | 0.28677 | 198 | 0.30175
142.2 | 0.1929 | 158 | 0.208 | 143.1 | 0.19022 | 159 | 0.20661 | 144.9 | 0.44902 | 161 | 0.46634 | 148.5 | 0.4254 | 165 | 0.44134 | 153 | 0.40047 | 170 | 0.41634 | 159.3 | 0.3631 | 177 | 0.37675 | 169.2 | 0.32131 | 188 | 0.33509 | 179.1 | 0.28327 | 199 | 0.29967
143.1 | 0.19053 | 159 | 0.208 | 144 | 0.18785 | 160 | 0.20245 | 145.8 | 0.44332 | 162 | 0.458 | 149.4 | 0.41999 | 166 | 0.43509 | 153.9 | 0.3953 | 171 | 0.41009 | 160.2 | 0.35914 | 178 | 0.37467 | 170.1 | 0.31745 | 189 | 0.333 | 180 | 0.27978 | 200 | 0.29342
144 | 0.18815 | 160 | 0.202 | 144.9 | 0.18547 | 161 | 0.20106 | 146.7 | 0.43763 | 163 | 0.45175 | 150.3 | 0.41457 | 167 | 0.42884 | 154.8 | 0.39013 | 172 | 0.40384 | 161.1 | 0.35517 | 179 | 0.36842 | 171 | 0.31358 | 190 | 0.32675 | 180.9 | 0.27686 | 201 | 0.29134
144.9 | 0.18576 | 161 | 0.201 | 145.8 | 0.1831 | 162 | 0.19967 | 147.6 | 0.43193 | 164 | 0.4455 | 151.2 | 0.40914 | 168 | 0.42467 | 155.7 | 0.38497 | 173 | 0.39967 | 162 | 0.35121 | 180 | 0.36634 | 171.9 | 0.30971 | 191 | 0.32467 | 181.8 | 0.2743 | 202 | 0.29134
145.8 | 0.18338 | 162 | 0.2 | 146.7 | 0.18071 | 163 | 0.19828 | 148.5 | 0.42624 | 165 | 0.44134 | 152.1 | 0.40372 | 169 | 0.41842 | 156.6 | 0.3798 | 174 | 0.39342 | 162.9 | 0.34723 | 181 | 0.36009 | 172.8 | 0.30608 | 192 | 0.3205 | 182.7 | 0.27176 | 203 | 0.28509
146.7 | 0.18099 | 163 | 0.198 | 147.6 | 0.17834 | 164 | 0.19342 | 149.4 | 0.42057 | 166 | 0.43509 | 153 | 0.39831 | 170 | 0.41217 | 157.5 | 0.37464 | 175 | 0.39134 | 163.8 | 0.34328 | 182 | 0.358 | 173.7 | 0.30309 | 193 | 0.31842 | 183.6 | 0.26919 | 204 | 0.283
147.6 | 0.17861 | 164 | 0.193 | 148.5 | 0.17597 | 165 | 0.19134 | 150.3 | 0.41488 | 167 | 0.42884 | 153.9 | 0.39288 | 171 | 0.408 | 158.4 | 0.36949 | 176 | 0.383 | 164.7 | 0.33932 | 183 | 0.35384 | 174.6 | 0.30008 | 194 | 0.31634 | 184.5 | 0.26665 | 205 | 0.283
148.5 | 0.17623 | 165 | 0.191 | 149.4 | 0.17362 | 166 | 0.18995 | 151.2 | 0.40918 | 168 | 0.42467 | 154.8 | 0.38746 | 172 | 0.40175 | 159.3 | 0.36451 | 177 | 0.37884 | 165.6 | 0.33535 | 184 | 0.34967 | 175.5 | 0.29709 | 195 | 0.31009 | 185.4 | 0.26408 | 206 | 0.27675
149.4 | 0.17386 | 166 | 0.191 | 150.3 | 0.17123 | 167 | 0.18578 | 152.1 | 0.4035 | 169 | 0.41842 | 155.7 | 0.38206 | 173 | 0.3955 | 160.2 | 0.36064 | 178 | 0.37467 | 166.5 | 0.33139 | 185 | 0.3455 | 176.4 | 0.29408 | 196 | 0.308 | 186.3 | 0.26155 | 207 | 0.27675
150.3 | 0.17147 | 167 | 0.186 | 151.2 | 0.16887 | 168 | 0.18439 | 153 | 0.39781 | 170 | 0.41217 | 156.6 | 0.37664 | 174 | 0.39134 | 161.1 | 0.35676 | 179 | 0.3705 | 167.4 | 0.32744 | 186 | 0.34134 | 177.3 | 0.2911 | 197 | 0.308 | 187.2 | 0.25899 | 208 | 0.27467
151.2 | 0.1691 | 168 | 0.184 | 152.1 | 0.16652 | 169 | 0.183 | 153.9 | 0.39213 | 171 | 0.408 | 157.5 | 0.37123 | 175 | 0.38509 | 162 | 0.35289 | 180 | 0.36634 | 168.3 | 0.32346 | 187 | 0.33717 | 178.2 | 0.28808 | 198 | 0.30175 | 188.1 | 0.25645 | 209 | 0.2705
152.1 | 0.16674 | 169 | 0.183 | 153 | 0.16415 | 170 | 0.18161 | 154.8 | 0.38644 | 172 | 0.39967 | 158.4 | 0.36595 | 176 | 0.383 | 162.9 | 0.34902 | 181 | 0.36634 | 169.2 | 0.31952 | 188 | 0.333 | 179.1 | 0.28509 | 199 | 0.29967 | 189 | 0.2539 | 210 | 0.26842
153 | 0.16437 | 170 | 0.182 | 153.9 | 0.16178 | 171 | 0.17675 | 155.7 | 0.38182 | 173 | 0.3955 | 159.3 | 0.36208 | 177 | 0.37675 | 163.8 | 0.34516 | 182 | 0.36009 | 170.1 | 0.31558 | 189 | 0.32884 | 180 | 0.28209 | 200 | 0.2955 | 189.9 | 0.25136 | 211 | 0.26634
153.9 | 0.162 | 171 | 0.177 | 154.8 | 0.15943 | 172 | 0.17467 | 156.6 | 0.37738 | 174 | 0.39134 | 160.2 | 0.35822 | 178 | 0.37467 | 164.7 | 0.3413 | 183 | 0.358 | 171 | 0.31163 | 190 | 0.32675 | 180.9 | 0.27911 | 201 | 0.29342 | 190.8 | 0.24882 | 212 | 0.26217
154.8 | 0.15963 | 172 | 0.176 | 155.7 | 0.15707 | 173 | 0.17467 | 157.5 | 0.37295 | 175 | 0.38717 | 161.1 | 0.35434 | 179 | 0.36842 | 165.6 | 0.33742 | 184 | 0.35175 | 171.9 | 0.30768 | 191 | 0.32467 | 181.8 | 0.27612 | 202 | 0.29134 | 191.7 | 0.24629 | 213 | 0.26009
155.7 | 0.15769 | 173 | 0.175 | 156.6 | 0.15512 | 174 | 0.16911 | 158.4 | 0.36853 | 176 | 0.383 | 162 | 0.35047 | 180 | 0.36634 | 166.5 | 0.33356 | 185 | 0.34967 | 172.8 | 0.30374 | 192 | 0.31842 | 182.7 | 0.27313 | 203 | 0.28717 | 192.6 | 0.24373 | 214 | 0.258
156.6 | 0.15589 | 174 | 0.173 | 157.5 | 0.15345 | 175 | 0.16842 | 159.3 | 0.3641 | 177 | 0.37884 | 162.9 | 0.34661 | 181 | 0.36009 | 167.4 | 0.32969 | 186 | 0.34342 | 173.7 | 0.30087 | 193 | 0.31634 | 183.6 | 0.27014 | 204 | 0.28509 | 193.5 | 0.2412 | 215 | 0.258
157.5 | 0.15408 | 175 | 0.169 | 158.4 | 0.15181 | 176 | 0.16773 | 160.2 | 0.35967 | 178 | 0.37467 | 163.8 | 0.34277 | 182 | 0.358 | 168.3 | 0.32581 | 187 | 0.34134 | 174.6 | 0.29798 | 194 | 0.31217 | 184.5 | 0.26716 | 205 | 0.283 | 194.4 | 0.23866 | 216 | 0.25175
158.4 | 0.15229 | 176 | 0.168 | 159.3 | 0.15016 | 177 | 0.16634 | 161.1 | 0.35525 | 179 | 0.36842 | 164.7 | 0.3389 | 183 | 0.35175 | 169.2 | 0.32195 | 188 | 0.33509 | 175.5 | 0.29511 | 195 | 0.31009 | 185.4 | 0.26415 | 206 | 0.27675 | 195.3 | 0.23613 | 217 | 0.24967
159.3 | 0.1505 | 177 | 0.166 | 160.2 | 0.1485 | 178 | 0.16495 | 162 | 0.35082 | 180 | 0.36634 | 165.6 | 0.33503 | 184 | 0.34967 | 170.1 | 0.31811 | 189 | 0.333 | 176.4 | 0.29221 | 196 | 0.308 | 186.3 | 0.26119 | 207 | 0.27467 | 196.2 | 0.23359 | 218 | 0.24967
160.2 | 0.1487 | 178 | 0.166 | 161.1 | 0.14684 | 179 | 0.16078 | 162.9 | 0.34639 | 181 | 0.36009 | 166.5 | 0.33118 | 185 | 0.3455 | 171 | 0.31423 | 190 | 0.32884 | 177.3 | 0.28935 | 197 | 0.30384 | 187.2 | 0.2582 | 208 | 0.27467 | 197.1 | 0.23105 | 219 | 0.2455
161.1 | 0.14689 | 179 | 0.161 | 162 | 0.14519 | 180 | 0.16009 | 163.8 | 0.34199 | 182 | 0.358 | 167.4 | 0.32731 | 186 | 0.34134 | 171.9 | 0.31038 | 191 | 0.32467 | 178.2 | 0.28645 | 198 | 0.30175 | 188.1 | 0.25553 | 209 | 0.26842 | 198 | 0.22854 | 220 | 0.24342
162 | 0.14511 | 180 | 0.16 | 162.9 | 0.14354 | 181 | 0.15939 | 164.7 | 0.33757 | 183 | 0.35175 | 168.3 | 0.32345 | 187 | 0.33717 | 172.8 | 0.30653 | 192 | 0.3205 | 179.1 | 0.28357 | 199 | 0.29967 | 189 | 0.25326 | 210 | 0.26842 | 198.9 | 0.22602 | 221 | 0.24134
162.9 | 0.14331 | 181 | 0.159 | 163.8 | 0.14189 | 182 | 0.158 | 165.6 | 0.33314 | 184 | 0.34967 | 169.2 | 0.3196 | 188 | 0.333 | 173.7 | 0.3035 | 193 | 0.31842 | 180 | 0.2807 | 200 | 0.29342 | 189.9 | 0.25101 | 211 | 0.26634 | 199.8 | 0.22423 | 222 | 0.24134
163.8 | 0.14151 | 182 | 0.158 | 164.7 | 0.14025 | 183 | 0.15661 | 166.5 | 0.32874 | 185 | 0.34342 | 170.1 | 0.31577 | 189 | 0.333 | 174.6 | 0.30048 | 194 | 0.31634 | 180.9 | 0.27784 | 201 | 0.29134 | 190.8 | 0.24875 | 212 | 0.26217 | 200.7 | 0.22244 | 223 | 0.23509
164.7 | 0.13973 | 183 | 0.157 | 165.6 | 0.13859 | 184 | 0.15245 | 167.4 | 0.32432 | 186 | 0.34134 | 171 | 0.31191 | 190 | 0.32675 | 175.5 | 0.29747 | 195 | 0.31009 | 181.8 | 0.27496 | 202 | 0.29134 | 191.7 | 0.24649 | 213 | 0.26009 | 201.6 | 0.22065 | 224 | 0.23509
165.6 | 0.13792 | 184 | 0.152 | 166.5 | 0.13695 | 185 | 0.15175 | 168.3 | 0.32094 | 187 | 0.33509 | 171.9 | 0.30805 | 191 | 0.32467 | 176.4 | 0.29443 | 196 | 0.308 | 182.7 | 0.27209 | 203 | 0.28509 | 192.6 | 0.24422 | 214 | 0.258 | 202.5 | 0.21887 | 225 | 0.233
166.5 | 0.13654 | 185 | 0.152 | 167.4 | 0.1353 | 186 | 0.15106 | 169.2 | 0.31771 | 188 | 0.333 | 172.8 | 0.30422 | 192 | 0.31842 | 177.3 | 0.29143 | 197 | 0.308 | 183.6 | 0.26921 | 204 | 0.283 | 193.5 | 0.24196 | 215 | 0.258 | 203.4 | 0.21709 | 226 | 0.233
167.4 | 0.13518 | 186 | 0.151 | 168.3 | 0.13366 | 187 | 0.14967 | 170.1 | 0.31449 | 189 | 0.32884 | 173.7 | 0.3013 | 193 | 0.31634 | 178.2 | 0.28841 | 198 | 0.30175 | 184.5 | 0.26635 | 205 | 0.283 | 194.4 | 0.23969 | 216 | 0.25384 | 204.3 | 0.2153 | 227 | 0.22884
168.3 | 0.13382 | 187 | 0.15 | 169.2 | 0.13201 | 188 | 0.14967 | 171 | 0.31124 | 190 | 0.32467 | 174.6 | 0.29839 | 194 | 0.31217 | 179.1 | 0.28539 | 199 | 0.29967 | 185.4 | 0.26347 | 206 | 0.27675 | 195.3 | 0.23743 | 217 | 0.25175 | 205.2 | 0.21353 | 228 | 0.22675
169.2 | 0.13246 | 188 | 0.15 | 170.1 | 0.13059 | 189 | 0.14828 | 171.9 | 0.30801 | 191 | 0.32467 | 175.5 | 0.29547 | 195 | 0.31009 | 180 | 0.28237 | 200 | 0.29967 | 186.3 | 0.26062 | 207 | 0.27467 | 196.2 | 0.23517 | 218 | 0.24967 | 206.1 | 0.21174 | 229 | 0.22675
170.1 | 0.1311 | 189 | 0.148 | 171 | 0.12933 | 190 | 0.14412 | 172.8 | 0.30478 | 192 | 0.31842 | 176.4 | 0.29254 | 196 | 0.308 | 180.9 | 0.27938 | 201 | 0.29342 | 187.2 | 0.25775 | 208 | 0.27467 | 197.1 | 0.23291 | 219 | 0.24967 | 207 | 0.20996 | 230 | 0.22467
171 | 0.12976 | 190 | 0.144 | 171.9 | 0.12808 | 191 | 0.14342 | 173.7 | 0.30154 | 193 | 0.31634 | 177.3 | 0.28964 | 197 | 0.30384 | 181.8 | 0.27636 | 202 | 0.29134 | 188.1 | 0.25507 | 209 | 0.26842 | 198 | 0.23066 | 220 | 0.24342 | 207.9 | 0.20817 | 231 | 0.22467
171.9 | 0.12841 | 191 | 0.143 | 172.8 | 0.12683 | 192 | 0.14273 | 174.6 | 0.29831 | 194 | 0.31217 | 178.2 | 0.28671 | 198 | 0.30175 | 182.7 | 0.27336 | 203 | 0.28717 | 189 | 0.25272 | 210 | 0.26634 | 198.9 | 0.22841 | 221 | 0.24342 | 208.8 | 0.20639 | 232 | 0.2205
172.8 | 0.12705 | 192 | 0.143 | 173.7 | 0.12557 | 193 | 0.14134 | 175.5 | 0.29508 | 195 | 0.31009 | 179.1 | 0.28379 | 199 | 0.29967 | 183.6 | 0.27034 | 204 | 0.28509 | 189.9 | 0.25038 | 211 | 0.26634 | 199.8 | 0.22615 | 222 | 0.24134 | 209.7 | 0.2046 | 233 | 0.21842
173.7 | 0.1257 | 193 | 0.141 | 174.6 | 0.12433 | 194 | 0.14134 | 176.4 | 0.29184 | 196 | 0.308 | 180 | 0.28088 | 200 | 0.2955 | 184.5 | 0.26734 | 205 | 0.283 | 190.8 | 0.24803 | 212 | 0.26217 | 200.7 | 0.2239 | 223 | 0.24134 | 210.6 | 0.20282 | 234 | 0.21634
174.6 | 0.12436 | 194 | 0.141 | 175.5 | 0.1231 | 195 | 0.13995 | 177.3 | 0.28863 | 197 | 0.30175 | 180.9 | 0.27798 | 201 | 0.29134 | 185.4 | 0.26431 | 206 | 0.27884 | 191.7 | 0.24569 | 213 | 0.26009 | 201.6 | 0.22165 | 224 | 0.23509 | 211.5 | 0.20103 | 235 | 0.21634
175.5 | 0.12302 | 195 | 0.14 | 176.4 | 0.12185 | 196 | 0.13578 | 178.2 | 0.28538 | 198 | 0.29967 | 181.8 | 0.27506 | 202 | 0.29134 | 186.3 | 0.26132 | 207 | 0.27467 | 192.6 | 0.24333 | 214 | 0.258 | 202.5 | 0.21941 | 225 | 0.233 | 212.4 | 0.19927 | 236 | 0.21634
176.4 | 0.12167 | 196 | 0.136 | 177.3 | 0.12062 | 197 | 0.13508 | 179.1 | 0.28217 | 199 | 0.2955 | 182.7 | 0.27216 | 203 | 0.28509 | 187.2 | 0.25832 | 208 | 0.27467 | 193.5 | 0.24098 | 215 | 0.258 | 203.4 | 0.21717 | 226 | 0.233 | 213.3 | 0.1975 | 237 | 0.21217
177.3 | 0.12035 | 197 | 0.135 | 178.2 | 0.11937 | 198 | 0.13439 | 180 | 0.27894 | 200 | 0.29342 | 183.6 | 0.26924 | 204 | 0.283 | 188.1 | 0.25532 | 209 | 0.26842 | 194.4 | 0.23863 | 216 | 0.25175 | 204.3 | 0.21493 | 227 | 0.22884 | 214.2 | 0.19572 | 238 | 0.21009
178.2 | 0.119 | 198 | 0.134 | 179.1 | 0.11813 | 199 | 0.13439 | 180.9 | 0.27631 | 201 | 0.29134 | 184.5 | 0.26634 | 205 | 0.283 | 189 | 0.25313 | 210 | 0.26842 | 195.3 | 0.23628 | 217 | 0.24967 | 205.2 | 0.21269 | 228 | 0.22675 | 215.1 | 0.19365 | 239 | 0.20939
179.1 | 0.11764 | 199 | 0.133 | 180 | 0.11688 | 200 | 0.133 | 181.8 | 0.27377 | 202 | 0.28717 | 185.4 | 0.26341 | 206 | 0.27675 | 189.9 | 0.25105 | 211 | 0.26634 | 196.2 | 0.23393 | 218 | 0.24967 | 206.1 | 0.21057 | 229 | 0.22467 | 216 | 0.19205 | 240 | 0.208
180 | 0.11662 | 200 | 0.133 | 180.9 | 0.11565 | 201 | 0.133 | 182.7 | 0.27125 | 203 | 0.28509 | 186.3 | 0.26053 | 207 | 0.27467 | 190.8 | 0.24895 | 212 | 0.26217 | 197.1 | 0.23159 | 219 | 0.2455 | 207 | 0.20895 | 230 | 0.22467 | 216.9 | 0.19075 | 241 | 0.208
180.9 | 0.11567 | 201 | 0.133 | 181.8 | 0.11441 | 202 | 0.13162 | 183.6 | 0.2687 | 204 | 0.283 | 187.2 | 0.25762 | 208 | 0.27467 | 191.7 | 0.24687 | 213 | 0.26009 | 198 | 0.22925 | 220 | 0.24342 | 207.9 | 0.20732 | 231 | 0.22467 | 217.8 | 0.18945 | 242 | 0.20661
181.8 | 0.11472 | 202 | 0.132 | 182.7 | 0.11316 | 203 | 0.12745 | 184.5 | 0.26618 | 205 | 0.283 | 188.1 | 0.25472 | 209 | 0.26842 | 192.6 | 0.24476 | 214 | 0.26009 | 198.9 | 0.22691 | 221 | 0.24134 | 208.8 | 0.20569 | 232 | 0.21842 | 218.7 | 0.18816 | 243 | 0.20245
182.7 | 0.11377 | 203 | 0.131 | 183.6 | 0.1123 | 204 | 0.12676 | 185.4 | 0.26362 | 206 | 0.27675 | 189 | 0.25181 | 210 | 0.26634 | 193.5 | 0.24267 | 215 | 0.258 | 199.8 | 0.22458 | 222 | 0.24134 | 209.7 | 0.20406 | 233 | 0.21842 | 219.6 | 0.18688 | 244 | 0.20175
183.6 | 0.11283 | 204 | 0.127 | 184.5 | 0.11145 | 205 | 0.12676 | 186.3 | 0.26111 | 207 | 0.27467 | 189.9 | 0.24892 | 211 | 0.26217 | 194.4 | 0.24058 | 216 | 0.25384 | 200.7 | 0.22223 | 223 | 0.23509 | 210.6 | 0.20243 | 234 | 0.21634 | 220.5 | 0.18559 | 245 | 0.20106
184.5 | 0.11188 | 205 | 0.127 | 185.4 | 0.11061 | 206 | 0.12606 | 187.2 | 0.25857 | 208 | 0.27467 | 190.8 | 0.2466 | 212 | 0.26009 | 195.3 | 0.23849 | 217 | 0.25175 | 201.6 | 0.2199 | 224 | 0.23509 | 211.5 | 0.2008 | 235 | 0.21634 | 221.4 | 0.18429 | 246 | 0.19967
185.4 | 0.11093 | 206 | 0.126 | 186.3 | 0.10977 | 207 | 0.12606 | 188.1 | 0.25605 | 209 | 0.2705 | 191.7 | 0.24445 | 213 | 0.258 | 196.2 | 0.23639 | 218 | 0.25175 | 202.5 | 0.21757 | 225 | 0.233 | 212.4 | 0.19919 | 236 | 0.21634 | 222.3 | 0.18301 | 247 | 0.19967
186.3 | 0.10999 | 207 | 0.126 | 187.2 | 0.10895 | 208 | 0.12467 | 189 | 0.25351 | 210 | 0.26842 | 192.6 | 0.2423 | 214 | 0.258 | 197.1 | 0.23429 | 219 | 0.24967 | 203.4 | 0.21555 | 226 | 0.22884 | 213.3 | 0.19756 | 237 | 0.21217 | 223.2 | 0.18173 | 248 | 0.19828
187.2 | 0.10905 | 208 | 0.125 | 188.1 | 0.10812 | 209 | 0.12467 | 189.9 | 0.25099 | 211 | 0.26634 | 193.5 | 0.24016 | 215 | 0.25384 | 198 | 0.23221 | 220 | 0.2455 | 204.3 | 0.21389 | 227 | 0.22675 | 214.2 | 0.19594 | 238 | 0.21009 | 224.1 | 0.18044 | 249 | 0.19759
188.1 | 0.10812 | 209 | 0.125 | 189 | 0.10728 | 210 | 0.12467 | 190.8 | 0.24847 | 212 | 0.26217 | 194.4 | 0.238 | 216 | 0.25175 | 198.9 | 0.23014 | 221 | 0.24342 | 205.2 | 0.21223 | 228 | 0.22675 | 215.1 | 0.19401 | 239 | 0.20939 | 225 | 0.17915 | 250 | 0.19411
189 | 0.10717 | 210 | 0.125 | 189.9 | 0.10645 | 211 | 0.12328 | 191.7 | 0.24596 | 213 | 0.26009 | 195.3 | 0.23586 | 217 | 0.24967 | 199.8 | 0.22805 | 222 | 0.24134 | 206.1 | 0.21055 | 229 | 0.22467 | 216 | 0.1924 | 240 | 0.208 | 225.9 | 0.17785 | 251 | 0.19342
189.9 | 0.10623 | 211 | 0.123 | 190.8 | 0.10562 | 212 | 0.12328 | 192.6 | 0.24342 | 214 | 0.258 | 196.2 | 0.23372 | 218 | 0.24967 | 200.7 | 0.22596 | 223 | 0.24134 | 207 | 0.20888 | 230 | 0.22467 | 216.9 | 0.19078 | 241 | 0.208 | 226.8 | 0.17656 | 252 | 0.19273
190.8 | 0.10529 | 212 | 0.119 | 191.7 | 0.1048 | 213 | 0.11911 | 193.5 | 0.2409 | 215 | 0.258 | 197.1 | 0.23157 | 219 | 0.2455 | 201.6 | 0.22388 | 224 | 0.23717 | 207.9 | 0.20722 | 231 | 0.22467 | 217.8 | 0.18916 | 242 | 0.20661 | 227.7 | 0.17529 | 253 | 0.19134
191.7 | 0.10436 | 213 | 0.119 | 192.6 | 0.10396 | 214 | 0.11841 | 194.4 | 0.23837 | 216 | 0.25175 | 198 | 0.22944 | 220 | 0.24342 | 202.5 | 0.2218 | 225 | 0.23509 | 208.8 | 0.20556 | 232 | 0.21842 | 218.7 | 0.18755 | 243 | 0.20245 | 228.6 | 0.17401 | 254 | 0.19134
192.6 | 0.10342 | 214 | 0.118 | 193.5 | 0.10314 | 215 | 0.11841 | 195.3 | 0.23586 | 217 | 0.24967 | 198.9 | 0.2273 | 221 | 0.24134 | 203.4 | 0.21974 | 226 | 0.23509 | 209.7 | 0.20389 | 233 | 0.21842 | 219.6 | 0.18594 | 244 | 0.20106 | 229.5 | 0.17273 | 255 | 0.18995
193.5 | 0.10249 | 215 | 0.118 | 194.4 | 0.10231 | 216 | 0.11772 | 196.2 | 0.23335 | 218 | 0.24967 | 199.8 | 0.22515 | 222 | 0.24134 | 204.3 | 0.21766 | 227 | 0.233 | 210.6 | 0.20223 | 234 | 0.21634 | 220.5 | 0.18432 | 245 | 0.19967 | 230.4 | 0.17144 | 256 | 0.18578
194.4 | 0.10155 | 216 | 0.118 | 195.3 | 0.10149 | 217 | 0.11772 | 197.1 | 0.23131 | 219 | 0.2455 | 200.7 | 0.22301 | 223 | 0.23717 | 205.2 | 0.21559 | 228 | 0.233 | 211.5 | 0.20055 | 235 | 0.21634 | 221.4 | 0.1827 | 246 | 0.19967 | 231.3 | 0.17016 | 257 | 0.18509
195.3 | 0.10061 | 217 | 0.116 | 196.2 | 0.10066 | 218 | 0.11634 | 198 | 0.22941 | 220 | 0.24342 | 201.6 | 0.22087 | 224 | 0.23509 | 206.1 | 0.21351 | 229 | 0.22675 | 212.4 | 0.1989 | 236 | 0.21634 | 222.3 | 0.18128 | 247 | 0.19828 | 232.2 | 0.16887 | 258 | 0.18439
196.2 | 0.099677 | 218 | 0.116 | 197.1 | 0.099843 | 219 | 0.11634 | 198.9 | 0.22751 | 221 | 0.24134 | 202.5 | 0.21875 | 225 | 0.233 | 207 | 0.21143 | 230 | 0.22675 | 213.3 | 0.19724 | 237 | 0.21009 | 223.2 | 0.1801 | 248 | 0.19411 | 233.1 | 0.16758 | 259 | 0.183
197.1 | 0.09876 | 219 | 0.116 | 198 | 0.099005 | 220 | 0.11634 | 199.8 | 0.2256 | 222 | 0.24134 | 203.4 | 0.21662 | 226 | 0.233 | 207.9 | 0.20936 | 231 | 0.22467 | 214.2 | 0.19558 | 238 | 0.21009 | 224.1 | 0.17891 | 249 | 0.19342 | 234 | 0.16631 | 260 | 0.183
198 | 0.098021 | 220 | 0.115 | 198.9 | 0.098195 | 221 | 0.11496 | 200.7 | 0.22369 | 223 | 0.23717 | 204.3 | 0.21449 | 227 | 0.22884 | 208.8 | 0.20729 | 232 | 0.22467 | 215.1 | 0.19364 | 239 | 0.20939 | 225 | 0.17773 | 250 | 0.19273 | 234.9 | 0.16502 | 261 | 0.18162
198.9 | 0.097365 | 221 | 0.115 | 199.8 | 0.097371 | 222 | 0.11496 | 201.6 | 0.22179 | 224 | 0.23509 | 205.2 | 0.21237 | 228 | 0.22675 | 209.7 | 0.20521 | 233 | 0.21842 | 216 | 0.19199 | 240 | 0.208 | 225.9 | 0.17654 | 251 | 0.19273 | 235.8 | 0.16375 | 262 | 0.17745
199.8 | 0.096684 | 222 | 0.111 | 200.7 | 0.096549 | 223 | 0.11079 | 202.5 | 0.21989 | 225 | 0.23509 | 206.1 | 0.21024 | 229 | 0.22467 | 210.6 | 0.20314 | 234 | 0.21842 | 216.9 | 0.19034 | 241 | 0.208 | 226.8 | 0.17536 | 252 | 0.19134 | 236.7 | 0.16247 | 263 | 0.17745
200.7 | 0.096011 | 223 | 0.111 | 201.6 | 0.095715 | 224 | 0.1101 | 203.4 | 0.21799 | 226 | 0.233 | 207 | 0.20811 | 230 | 0.22467 | 211.5 | 0.20106 | 235 | 0.21634 | 217.8 | 0.18867 | 242 | 0.20245 | 227.7 | 0.17419 | 253 | 0.19134 | 237.6 | 0.16119 | 264 | 0.17675
201.6 | 0.095336 | 224 | 0.11 | 202.5 | 0.094903 | 225 | 0.1101 | 204.3 | 0.21609 | 227 | 0.233 | 207.9 | 0.20664 | 231 | 0.2205 | 212.4 | 0.19907 | 236 | 0.21634 | 218.7 | 0.18703 | 243 | 0.20175 | 228.6 | 0.17302 | 254 | 0.18995 | 238.5 | 0.15992 | 265 | 0.17606
202.5 | 0.094673 | 225 | 0.11 | 203.4 | 0.094086 | 226 | 0.1094 | 205.2 | 0.2142 | 228 | 0.22884 | 208.8 | 0.2052 | 232 | 0.21842 | 213.3 | 0.19761 | 237 | 0.21217 | 219.6 | 0.18546 | 244 | 0.20106 | 229.5 | 0.17185 | 255 | 0.18578 | 239.4 | 0.15864 | 266 | 0.17467
203.4 | 0.094014 | 226 | 0.109 | 204.3 | 0.093258 | 227 | 0.1094 | 206.1 | 0.21228 | 229 | 0.22675 | 209.7 | 0.20375 | 233 | 0.21842 | 214.2 | 0.19616 | 238 | 0.21009 | 220.5 | 0.18422 | 245 | 0.19967 | 230.4 | 0.17067 | 256 | 0.18509 | 240.3 | 0.15736 | 267 | 0.17467
204.3 | 0.093338 | 227 | 0.109 | 205.2 | 0.092467 | 228 | 0.108 | 207 | 0.21039 | 230 | 0.22467 | 210.6 | 0.20231 | 234 | 0.21634 | 215.1 | 0.19438 | 239 | 0.20939 | 221.4 | 0.18299 | 246 | 0.19967 | 231.3 | 0.1695 | 257 | 0.18509 | 241.2 | 0.15609 | 268 | 0.17328
205.2 | 0.092678 | 228 | 0.108 | 206.1 | 0.091848 | 229 | 0.108 | 207.9 | 0.20848 | 231 | 0.22467 | 211.5 | 0.20086 | 235 | 0.21634 | 216 | 0.19295 | 240 | 0.20939 | 222.3 | 0.18177 | 247 | 0.19828 | 232.2 | 0.16831 | 258 | 0.18439 | 242.1 | 0.1548 | 269 | 0.16911
206.1 | 0.092008 | 229 | 0.108 | 207 | 0.091246 | 230 | 0.108 | 208.8 | 0.20659 | 232 | 0.2205 | 212.4 | 0.19943 | 236 | 0.21634 | 216.9 | 0.19149 | 241 | 0.208 | 223.2 | 0.18056 | 248 | 0.19828 | 233.1 | 0.16713 | 259 | 0.183 | 243 | 0.15353 | 270 | 0.16842
207 | 0.091353 | 230 | 0.108 | 207.9 | 0.090626 | 231 | 0.108 | 209.7 | 0.20468 | 233 | 0.21842 | 213.3 | 0.19799 | 237 | 0.21217 | 217.8 | 0.19005 | 242 | 0.20661 | 224.1 | 0.17932 | 249 | 0.19411 | 234 | 0.16596 | 260 | 0.183 | 243.9 | 0.15239 | 271 | 0.16773
207.9 | 0.090685 | 231 | 0.108 | 208.8 | 0.090025 | 232 | 0.1066 | 210.6 | 0.20278 | 234 | 0.21634 | 214.2 | 0.19656 | 238 | 0.21009 | 218.7 | 0.18861 | 243 | 0.20245 | 225 | 0.17811 | 250 | 0.19342 | 234.9 | 0.16479 | 261 | 0.18162 | 244.8 | 0.15152 | 272 | 0.16773
208.8 | 0.090029 | 232 | 0.107 | 209.7 | 0.089419 | 233 | 0.1066 | 211.5 | 0.20089 | 235 | 0.21634 | 215.1 | 0.19481 | 239 | 0.21009 | 219.6 | 0.18717 | 244 | 0.20175 | 225.9 | 0.17688 | 251 | 0.19273 | 235.8 | 0.16363 | 262 | 0.17745 | 245.7 | 0.15064 | 273 | 0.16634
209.7 | 0.089358 | 233 | 0.107 | 210.6 | 0.088819 | 234 | 0.10591 | 212.4 | 0.19901 | 236 | 0.21634 | 216 | 0.19339 | 240 | 0.20939 | 220.5 | 0.18573 | 245 | 0.20106 | 226.8 | 0.17566 | 252 | 0.19134 | 236.7 | 0.16245 | 263 | 0.17745 | 246.6 | 0.14977 | 274 | 0.16634
210.6 | 0.088703 | 234 | 0.102 | 211.5 | 0.088206 | 235 | 0.10243 | 213.3 | 0.19718 | 237 | 0.21009 | 216.9 | 0.19196 | 241 | 0.208 | 221.4 | 0.18428 | 246 | 0.19967 | 227.7 | 0.17446 | 253 | 0.19134 | 237.6 | 0.16128 | 264 | 0.17675 | 247.5 | 0.1489 | 275 | 0.16634
211.5 | 0.088042 | 235 | 0.102 | 212.4 | 0.087618 | 236 | 0.10243 | 214.2 | 0.19582 | 238 | 0.21009 | 217.8 | 0.19052 | 242 | 0.208 | 222.3 | 0.18285 | 247 | 0.19967 | 228.6 | 0.17323 | 254 | 0.18995 | 238.5 | 0.16011 | 265 | 0.17606 | 248.4 | 0.14803 | 276 | 0.16495
212.4 | 0.087397 | 236 | 0.102 | 213.3 | 0.087013 | 237 | 0.10174 | 215.1 | 0.19414 | 239 | 0.20939 | 218.7 | 0.1891 | 243 | 0.20661 | 223.2 | 0.18141 | 248 | 0.19828 | 229.5 | 0.17202 | 255 | 0.18578 | 239.4 | 0.15894 | 266 | 0.17467 | 249.3 | 0.14717 | 277 | 0.16425
213.3 | 0.086727 | 237 | 0.102 | 214.2 | 0.086408 | 238 | 0.10174 | 216 | 0.19277 | 240 | 0.208 | 219.6 | 0.18767 | 244 | 0.20245 | 224.1 | 0.17997 | 249 | 0.19411 | 230.4 | 0.1708 | 256 | 0.18578 | 240.3 | 0.15777 | 267 | 0.17467 | 250.2 | 0.1463 | 278 | 0.16078
214.2 | 0.086065 | 238 | 0.101 | 215.1 | 0.085798 | 239 | 0.10105 | 216.9 | 0.19141 | 241 | 0.208 | 220.5 | 0.18625 | 245 | 0.20175 | 225 | 0.17854 | 250 | 0.19342 | 231.3 | 0.16959 | 257 | 0.18509 | 241.2 | 0.1566 | 268 | 0.17328 | 250.2 | 0.0072687 | 279 | 0.16009
215.1 | 0.085482 | 239 | 0.101 | 216 | 0.085212 | 240 | 0.10105 | 217.8 | 0.19004 | 242 | 0.20661 | 221.4 | 0.18481 | 246 | 0.20106 | 225.9 | 0.17709 | 251 | 0.19273 | 232.2 | 0.16836 | 258 | 0.18439 | 242.1 | 0.15542 | 269 | 0.16911 | 288 | 0.0067981 | 280 | 0.16009
216 | 0.084931 | 240 | 0.101 | 216.9 | 0.084602 | 241 | 0.099673 | 218.7 | 0.18869 | 243 | 0.20245 | 222.3 | 0.1834 | 247 | 0.19967 | 226.8 | 0.17565 | 252 | 0.19134 | 233.1 | 0.16714 | 259 | 0.183 | 243 | 0.15426 | 270 | 0.16911 | 297 | 0.0064401 | 281 | 0.15939
216.9 | 0.084367 | 241 | 0.1 | 217.8 | 0.083993 | 242 | 0.099673 | 219.6 | 0.18734 | 244 | 0.20175 | 223.2 | 0.18198 | 248 | 0.19967 | 227.7 | 0.17423 | 253 | 0.19134 | 234 | 0.16594 | 260 | 0.183 | 243.9 | 0.15309 | 271 | 0.16842 | 306 | 0.0061667 | 282 | 0.158
217.8 | 0.083806 | 242 | 0.1 | 218.7 | 0.083399 | 243 | 0.099673 | 220.5 | 0.18597 | 245 | 0.20106 | 224.1 | 0.18054 | 249 | 0.19759 | 228.6 | 0.17279 | 254 | 0.18995 | 234.9 | 0.16472 | 261 | 0.18162 | 244.8 | 0.15193 | 272 | 0.16773 | 315 | 0.0058962 | 283 | 0.158
218.7 | 0.083259 | 243 | 0.1 | 219.6 | 0.082808 | 244 | 0.099673 | 221.4 | 0.18461 | 246 | 0.20106 | 225 | 0.17912 | 250 | 0.19411 | 229.5 | 0.17144 | 255 | 0.18578 | 235.8 | 0.16352 | 262 | 0.17745 | 245.7 | 0.15076 | 273 | 0.16634 | 324 | 0.0056779 | 284 | 0.158
219.6 | 0.082707 | 244 | 0.1 | 220.5 | 0.082206 | 245 | 0.099673 | 222.3 | 0.18327 | 247 | 0.19967 | 225.9 | 0.17769 | 251 | 0.19273 | 230.4 | 0.17037 | 256 | 0.18509 | 236.7 | 0.1623 | 263 | 0.17675 | 246.6 | 0.14972 | 274 | 0.16634 | 333 | 0.0054841 | 285 | 0.158
220.5 | 0.082152 | 245 | 0.1 | 221.4 | 0.081599 | 246 | 0.098297 | 223.2 | 0.18192 | 248 | 0.19828 | 226.8 | 0.17626 | 252 | 0.19273 | 231.3 | 0.16931 | 257 | 0.18439 | 237.6 | 0.16109 | 264 | 0.17606 | 247.5 | 0.14889 | 275 | 0.16634 | 342 | 0.0053097 | 286 | 0.15661
221.4 | 0.08159 | 246 | 0.098 | 222.3 | 0.081022 | 247 | 0.098297 | 224.1 | 0.18055 | 249 | 0.19828 | 227.7 | 0.17485 | 253 | 0.19134 | 232.2 | 0.16823 | 258 | 0.18439 | 238.5 | 0.15988 | 265 | 0.17606 | 248.4 | 0.14805 | 276 | 0.16495 | 351 | 0.0051517 | 287 | 0.15245
222.3 | 0.081048 | 247 | 0.098 | 223.2 | 0.080425 | 248 | 0.097608 | 225 | 0.1792 | 250 | 0.19411 | 228.6 | 0.17342 | 254 | 0.18995 | 233.1 | 0.16716 | 259 | 0.183 | 239.4 | 0.15867 | 266 | 0.17467 | 249.3 | 0.14721 | 277 | 0.16495 | 360 | 0.0050073 | 288 | 0.15245
223.2 | 0.080496 | 248 | 0.098 | 224.1 | 0.079822 | 249 | 0.09414 | 225.9 | 0.17784 | 251 | 0.19342 | 229.5 | 0.17201 | 255 | 0.18578 | 234 | 0.16611 | 260 | 0.183 | 240.3 | 0.15746 | 267 | 0.17467 | 250.2 | 0.14639 | 278 | 0.16078 | 369 | 0.0048746 | 289 | 0.15175
224.1 | 0.079937 | 249 | 0.094 | 225 | 0.07923 | 250 | 0.09414 | 226.8 | 0.17648 | 252 | 0.19273 | 230.4 | 0.17057 | 256 | 0.18509 | 234.9 | 0.16504 | 261 | 0.18162 | 241.2 | 0.15625 | 268 | 0.17328 | 250.2 | 0.0072687 | 279 | 0.16009 | 378 | 0.0047517 | 290 | 0.15106
225 | 0.07939 | 250 | 0.094 | 225.9 | 0.078706 | 251 | 0.09344 | 227.7 | 0.17513 | 253 | 0.19134 | 231.3 | 0.16916 | 257 | 0.18439 | 235.8 | 0.16399 | 262 | 0.18161 | 242.1 | 0.15503 | 269 | 0.16911 | 288 | 0.0067981 | 280 | 0.16009 | 387 | 0.0046377 | 291 | 0.15106
225.9 | 0.07884 | 251 | 0.093 | 226.8 | 0.078267 | 252 | 0.09344 | 228.6 | 0.17378 | 254 | 0.19134 | 232.2 | 0.16773 | 258 | 0.183 | 236.7 | 0.16292 | 263 | 0.17745 | 243 | 0.15383 | 270 | 0.16842 | 297 | 0.0064401 | 281 | 0.15939 | 396 | 0.0040105 | 292 | 0.14967
226.8 | 0.078286 | 252 | 0.093 | 227.7 | 0.077844 | 253 | 0.09344 | 229.5 | 0.17243 | 255 | 0.18995 | 233.1 | 0.16631 | 259 | 0.183 | 237.6 | 0.16187 | 264 | 0.17675 | 243.9 | 0.15262 | 271 | 0.16773 | 306 | 0.0061667 | 282 | 0.15939 | 405 | 0.003911 | 293 | 0.14967
227.7 | 0.077747 | 253 | 0.093 | 228.6 | 0.077411 | 254 | 0.092739 | 230.4 | 0.17107 | 256 | 0.18578 | 234 | 0.16521 | 260 | 0.18161 | 238.5 | 0.1608 | 265 | 0.17606 | 244.8 | 0.15162 | 272 | 0.16773 | 315 | 0.0058962 | 283 | 0.158 | 414 | 0.0038178 | 294 | 0.14967
228.6 | 0.077197 | 254 | 0.093 | 229.5 | 0.076979 | 255 | 0.092739 | 231.3 | 0.16972 | 257 | 0.18509 | 234.9 | 0.16421 | 261 | 0.18161 | 239.4 | 0.15975 | 266 | 0.17606 | 245.7 | 0.15073 | 273 | 0.16634 | 324 | 0.0056779 | 284 | 0.158 | 423 | 0.0037299 | 295 | 0.14828
229.5 | 0.076646 | 255 | 0.093 | 230.4 | 0.076543 | 256 | 0.092739 | 232.2 | 0.16836 | 258 | 0.18439 | 235.8 | 0.16322 | 262 | 0.17745 | 240.3 | 0.15868 | 267 | 0.17467 | 246.6 | 0.14985 | 274 | 0.16634 | 333 | 0.0054841 | 285 | 0.158 | 432 | 0.0036472 | 296 | 0.14828
230.4 | 0.076198 | 256 | 0.091 | 231.3 | 0.076124 | 257 | 0.091332 | 233.1 | 0.16701 | 259 | 0.183 | 236.7 | 0.16222 | 263 | 0.17675 | 241.2 | 0.15763 | 268 | 0.17467 | 247.5 | 0.14898 | 275 | 0.16634 | 342 | 0.0053097 | 286 | 0.15661 | 441 | 0.003569 | 297 | 0.14412
231.3 | 0.075776 | 257 | 0.091 | 232.2 | 0.075685 | 258 | 0.091332 | 234 | 0.16566 | 260 | 0.183 | 237.6 | 0.16124 | 264 | 0.17675 | 242.1 | 0.15655 | 269 | 0.17328 | 248.4 | 0.1481 | 276 | 0.16495 | 351 | 0.0051517 | 287 | 0.15661 | 450 | 0.0034949 | 298 | 0.14273
232.2 | 0.075333 | 258 | 0.091 | 233.1 | 0.075253 | 259 | 0.091333 | 234.9 | 0.16431 | 261 | 0.18161 | 238.5 | 0.16025 | 265 | 0.17606 | 243 | 0.15551 | 270 | 0.17259 | 249.3 | 0.14722 | 277 | 0.16495 | 360 | 0.0050073 | 288 | 0.15245 | 459 | 0.0034246 | 300 | 0.14273
233.1 | 0.074901 | 259 | 0.091 | 234 | 0.07483 | 260 | 0.091333 | 235.8 | 0.16297 | 262 | 0.17745 | 239.4 | 0.15927 | 266 | 0.17467 | 243.9 | 0.15445 | 271 | 0.16911 | 250.2 | 0.14635 | 278 | 0.16078 | 369 | 0.0048746 | 289 | 0.15175 | 468 | 0.0030417 | 300 | 0.06
234 | 0.074479 | 260 | 0.091 | 234.9 | 0.0744 | 261 | 0.091333 | 236.7 | 0.16167 | 263 | 0.17675 | 240.3 | 0.15828 | 267 | 0.17467 | 244.8 | 0.1534 | 272 | 0.16842 | 250.2 | 0.0072687 | 279 | 0.16009 | 378 | 0.0047517 | 290 | 0.15175 | 6300 | 0.003 | 500 | 0.057
234.9 | 0.074051 | 261 | 0.091 | 235.8 | 0.073986 | 262 | 0.091332 | 237.6 | 0.16071 | 264 | 0.17606 | 241.2 | 0.15729 | 268 | 0.17467 | 245.7 | 0.15234 | 273 | 0.16773 | 288 | 0.0067981 | 280 | 0.16009 | 387 | 0.0046377 | 291 | 0.15106 |  |  | 500 | 0.033
235.8 | 0.073636 | 262 | 0.091 | 236.7 | 0.073551 | 263 | 0.089925 | 238.5 | 0.15976 | 265 | 0.17606 | 242.1 | 0.1563 | 269 | 0.17328 | 246.6 | 0.15129 | 274 | 0.16634 | 297 | 0.0064401 | 281 | 0.15939 | 396 | 0.0040105 | 292 | 0.15106 |  |  | 1000 | 0.033
236.7 | 0.073213 | 263 | 0.09 | 237.6 | 0.073131 | 264 | 0.089925 | 239.4 | 0.15879 | 266 | 0.17467 | 243 | 0.15531 | 270 | 0.16911 | 247.5 | 0.15023 | 275 | 0.16634 | 306 | 0.0061667 | 282 | 0.158 | 405 | 0.003911 | 293 | 0.14967 |  |  | 6300 | 0.022
237.6 | 0.072792 | 264 | 0.09 | 238.5 | 0.072709 | 265 | 0.089925 | 240.3 | 0.15782 | 267 | 0.17467 | 243.9 | 0.15432 | 271 | 0.16911 | 248.4 | 0.14918 | 276 | 0.16634 | 315 | 0.0058962 | 283 | 0.158 | 414 | 0.0038178 | 294 | 0.14967
238.5 | 0.07237 | 265 | 0.09 | 239.4 | 0.072288 | 266 | 0.089925 | 241.2 | 0.15687 | 268 | 0.17328 | 244.8 | 0.15334 | 272 | 0.16842 | 249.3 | 0.14812 | 277 | 0.16495 | 324 | 0.0056779 | 284 | 0.158 | 423 | 0.0037299 | 295 | 0.14967
239.4 | 0.071948 | 266 | 0.086 | 240.3 | 0.071862 | 267 | 0.085744 | 242.1 | 0.1559 | 269 | 0.17328 | 245.7 | 0.15236 | 273 | 0.16773 | 250.2 | 0.14707 | 278 | 0.16078 | 333 | 0.0054841 | 285 | 0.158 | 432 | 0.0036472 | 296 | 0.14828
240.3 | 0.071521 | 267 | 0.086 | 241.2 | 0.071443 | 268 | 0.085744 | 243 | 0.15495 | 270 | 0.16911 | 246.6 | 0.15138 | 274 | 0.16773 | 250.2 | 0.0072687 | 279 | 0.16078 | 342 | 0.0053097 | 286 | 0.15661 | 441 | 0.003569 | 297 | 0.14412
241.2 | 0.071101 | 268 | 0.086 | 242.1 | 0.071013 | 269 | 0.085744 | 243.9 | 0.15399 | 271 | 0.16842 | 247.5 | 0.15039 | 275 | 0.16634 | 288 | 0.0067981 | 280 | 0.16009 | 351 | 0.0051517 | 287 | 0.15245 | 450 | 0.0034949 | 298 | 0.14412
242.1 | 0.07067 | 269 | 0.085 | 243 | 0.070596 | 270 | 0.085057 | 244.8 | 0.15303 | 272 | 0.16842 | 248.4 | 0.14941 | 276 | 0.16634 | 297 | 0.0064401 | 281 | 0.15939 | 360 | 0.0050073 | 288 | 0.15245 | 459 | 0.0034246 | 300 | 0.14273
243 | 0.070252 | 270 | 0.085 | 243.9 | 0.070174 | 271 | 0.085057 | 245.7 | 0.15208 | 273 | 0.16773 | 249.3 | 0.14843 | 277 | 0.16495 | 306 | 0.0061667 | 282 | 0.158 | 369 | 0.0048746 | 289 | 0.15175 | 468 | 0.003 | 300 | 0.06
243.9 | 0.069839 | 271 | 0.085 | 244.8 | 0.069757 | 272 | 0.085057 | 246.6 | 0.15112 | 274 | 0.16634 | 250.2 | 0.14745 | 278 | 0.16495 | 315 | 0.0058962 | 283 | 0.158 | 378 | 0.0047517 | 290 | 0.15106 | 6300 | 0.003 | 500 | 0.057
244.8 | 0.069421 | 272 | 0.084 | 245.7 | 0.069333 | 273 | 0.084373 | 247.5 | 0.15017 | 275 | 0.16634 | 250.2 | 0.0072687 | 279 | 0.16078 | 324 | 0.0056779 | 284 | 0.158 | 387 | 0.0046377 | 291 | 0.15106 |  |  | 500 | 0.033
245.7 | 0.068996 | 273 | 0.084 | 246.6 | 0.068914 | 274 | 0.084373 | 248.4 | 0.1492 | 276 | 0.16634 | 288 | 0.0067981 | 280 | 0.16009 | 333 | 0.0054841 | 285 | 0.15661 | 396 | 0.0040105 | 292 | 0.14967 |  |  | 1000 | 0.033
246.6 | 0.068577 | 274 | 0.084 | 247.5 | 0.068496 | 275 | 0.084373 | 249.3 | 0.14825 | 277 | 0.16495 | 297 | 0.0064401 | 281 | 0.15939 | 342 | 0.0053097 | 286 | 0.15661 | 405 | 0.003911 | 293 | 0.14967 |  |  | 6300 | 0.022
247.5 | 0.068159 | 275 | 0.084 | 248.4 | 0.068075 | 276 | 0.08301 | 250.2 | 0.1473 | 278 | 0.16495 | 306 | 0.0061667 | 282 | 0.15939 | 351 | 0.0051517 | 287 | 0.15245 | 414 | 0.0038178 | 294 | 0.14967
248.4 | 0.067737 | 276 | 0.083 | 249.3 | 0.067655 | 277 | 0.08301 | 250.2 | 0.0072687 | 279 | 0.16078 | 315 | 0.0058962 | 283 | 0.158 | 360 | 0.0050073 | 288 | 0.15245 | 423 | 0.0037299 | 295 | 0.14828
249.3 | 0.067315 | 277 | 0.083 | 250.2 | 0.06724 | 278 | 0.08301 | 288 | 0.0067981 | 280 | 0.16009 | 324 | 0.0056779 | 284 | 0.158 | 369 | 0.0048746 | 289 | 0.15175 | 432 | 0.0036472 | 296 | 0.14828
250.2 | 0.066927 | 278 | 0.083 | 250.2 | 0.0072687 | 279 | 0.08301 | 297 | 0.0064401 | 281 | 0.15939 | 333 | 0.0054841 | 285 | 0.158 | 378 | 0.0047517 | 290 | 0.15106 | 441 | 0.003569 | 297 | 0.14412
250.2 | 0.0072687 | 279 | 0.083 | 288 | 0.0067981 | 280 | 0.08301 | 306 | 0.0061667 | 282 | 0.15939 | 342 | 0.0053097 | 286 | 0.15661 | 387 | 0.0046377 | 291 | 0.15106 | 450 | 0.0034949 | 298 | 0.14273
468 | 0.003 | 280 | 0.083 | 297 | 0.0064401 | 281 | 0.08301 | 315 | 0.0058962 | 283 | 0.158 | 351 | 0.0051517 | 287 | 0.15245 | 396 | 0.0040105 | 292 | 0.14967 | 459 | 0.0034246 | 300 | 0.14273
6300 | 0.003 | 281 | 0.083 | 306 | 0.0061667 | 282 | 0.08301 | 324 | 0.0056779 | 284 | 0.158 | 360 | 0.0050073 | 288 | 0.15245 | 405 | 0.003911 | 293 | 0.14967 | 468 | 0.003 | 300 | 0.06
|  | 282 | 0.083 | 315 | 0.0058962 | 283 | 0.081649 | 333 | 0.0054841 | 285 | 0.158 | 369 | 0.0048746 | 289 | 0.15175 | 414 | 0.0038178 | 294 | 0.14967 | 6300 | 0.003 | 500 | 0.057
|  | 283 | 0.083 | 324 | 0.0056779 | 284 | 0.081649 | 342 | 0.0053097 | 286 | 0.15661 | 378 | 0.0047517 | 290 | 0.15106 | 423 | 0.0037299 | 295 | 0.14967 |  |  | 500 | 0.033
|  | 284 | 0.082 | 333 | 0.0054841 | 285 | 0.081649 | 351 | 0.0051517 | 287 | 0.15245 | 387 | 0.0046377 | 291 | 0.15106 | 432 | 0.0036472 | 296 | 0.14828 |  |  | 1000 | 0.033
|  | 285 | 0.082 | 342 | 0.0053097 | 286 | 0.081649 | 360 | 0.0050073 | 288 | 0.15245 | 396 | 0.0040105 | 292 | 0.14967 | 441 | 0.003569 | 297 | 0.14412 |  |  | 6300 | 0.022
|  | 286 | 0.082 | 351 | 0.0051517 | 287 | 0.081649 | 369 | 0.0048746 | 289 | 0.15175 | 405 | 0.003911 | 293 | 0.14967 | 450 | 0.0034949 | 298 | 0.14412
|  | 287 | 0.082 | 360 | 0.0050073 | 288 | 0.080966 | 378 | 0.0047517 | 290 | 0.15106 | 414 | 0.0038178 | 294 | 0.14967 | 459 | 0.0034246 | 300 | 0.14273
|  | 288 | 0.078 | 369 | 0.0048746 | 289 | 0.077503 | 387 | 0.0046377 | 291 | 0.15106 | 423 | 0.0037299 | 295 | 0.14828 | 468 | 0.003 | 300 | 0.06
|  | 289 | 0.078 | 378 | 0.0047517 | 290 | 0.077503 | 396 | 0.0040105 | 292 | 0.14967 | 432 | 0.0036472 | 296 | 0.14828 | 6300 | 0.003 | 500 | 0.057
|  | 290 | 0.078 | 387 | 0.0046377 | 291 | 0.077503 | 405 | 0.003911 | 293 | 0.14967 | 441 | 0.003569 | 297 | 0.14412 |  |  | 500 | 0.033
|  | 291 | 0.078 | 396 | 0.0040105 | 292 | 0.077503 | 414 | 0.0038178 | 294 | 0.14967 | 450 | 0.0034949 | 298 | 0.14342 |  |  | 1000 | 0.033
|  | 292 | 0.077 | 405 | 0.003911 | 293 | 0.076797 | 423 | 0.0037299 | 295 | 0.14967 | 459 | 0.0034246 | 300 | 0.14273 |  |  | 6300 | 0.022
|  | 293 | 0.077 | 414 | 0.0038178 | 294 | 0.076797 | 432 | 0.0036472 | 296 | 0.14828 | 468 | 0.003 | 300 | 0.06
|  | 294 | 0.077 | 423 | 0.0037299 | 295 | 0.076797 | 441 | 0.003569 | 297 | 0.14412 | 6300 | 0.003 | 500 | 0.057
|  | 295 | 0.077 | 432 | 0.0036472 | 296 | 0.076797 | 450 | 0.0034949 | 298 | 0.14412 |  |  | 500 | 0.033
|  | 296 | 0.076 | 441 | 0.003569 | 297 | 0.076088 | 459 | 0.0034246 | 300 | 0.14273 |  |  | 1000 | 0.033
|  | 297 | 0.076 | 450 | 0.0034949 | 298 | 0.076088 | 468 | 0.003 | 300 | 0.06 |  |  | 6300 | 0.022
|  | 298 | 0.076 | 459 | 0.0034246 | 300 | 0.076 | 6300 | 0.003 | 500 | 0.057
|  | 300 | 0.076 | 468 | 0.003 | 300 | 0.06 |  |  | 500 | 0.033
|  | 300 | 0.06 | 6300 | 0.003 | 500 | 0.057 |  |  | 1000 | 0.033
|  | 500 | 0.057 |  |  | 500 | 0.033 |  |  | 6300 | 0.022
|  | 500 | 0.033 |  |  | 1000 | 0.033
|  | 1000 | 0.033 |  |  | 6300 | 0.022
|  | 6300 | 0.022

## S&C "NK" Speed
S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter
S&C "NK" Speed | [11 empty] | S&C "NK" Speed | [11 empty] | S&C "NK" Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025
Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information.
2NK |  |  |  | 3NK |  |  |  | 5NK |  |  |  | 7NK |  |  |  | 10NK |  |  |  | 15NK |  |  |  | 20NK
Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s
4 | 145.018 | 5 | 145.034 | 7 | 87.873 | 8 | 87.889 | 9 | 17.175 | 10 | 17.191 | 12.6 | 71.699 | 14 | 71.715 | 18 | 89.92 | 20 | 89.9358 | 24.3 | 1063.22 | 27 | 1063.236 | 32.4 | 2000.885 | 36 | 2000.902
5 | 49.013 | 6 | 49.027 | 8 | 15.913 | 9 | 15.927 | 9.9 | 8.01 | 11 | 8.027 | 13.5 | 30.539 | 15 | 30.552 | 18.9 | 36.482 | 21 | 36.4955 | 25.2 | 92.225 | 28 | 92.241 | 33.3 | 148.325 | 37 | 148.341
6 | 32.013 | 7 | 32.027 | 9 | 5.705 | 10 | 5.718 | 10.8 | 5.059 | 12 | 5.075 | 14.4 | 18.929 | 16 | 18.943 | 19.8 | 22.478 | 22 | 22.4934 | 26.1 | 47.389 | 29 | 47.404 | 34.2 | 74.639 | 38 | 74.654
7 | 25.012 | 8 | 25.027 | 9.9 | 3.91 | 11 | 3.925 | 11.7 | 3.614 | 13 | 3.627 | 15.3 | 13.477 | 17 | 13.491 | 20.7 | 16.038 | 23 | 16.0518 | 27 | 31.528 | 30 | 31.543 | 35.1 | 49.433 | 39 | 49.45
8 | 21.011 | 9 | 21.025 | 10.8 | 2.805 | 12 | 2.818 | 12.6 | 2.763 | 14 | 2.777 | 16.2 | 10.325 | 18 | 10.341 | 21.6 | 12.346 | 24 | 12.3601 | 27.9 | 23.424 | 31 | 23.437 | 36 | 36.715 | 40 | 36.729
9 | 5.68 | 10 | 5.693 | 11.7 | 2.307 | 13 | 2.321 | 13.5 | 2.206 | 15 | 2.221 | 17.1 | 8.279 | 19 | 8.293 | 22.5 | 9.957 | 25 | 9.9705 | 28.8 | 18.511 | 32 | 18.527 | 36.9 | 29.052 | 41 | 29.068
9.9 | 3.676 | 11 | 3.691 | 12.6 | 1.925 | 14 | 1.941 | 14.4 | 1.816 | 16 | 1.833 | 18 | 6.849 | 20 | 6.866 | 23.4 | 8.289 | 26 | 8.3018 | 29.7 | 15.219 | 33 | 15.235 | 37.8 | 23.934 | 42 | 23.95
10.8 | 2.689 | 12 | 2.702 | 13.5 | 1.626 | 15 | 1.641 | 15.3 | 1.529 | 17 | 1.543 | 18.9 | 5.797 | 21 | 5.81 | 24.3 | 7.06 | 27 | 7.0747 | 30.6 | 12.862 | 34 | 12.877 | 38.7 | 20.277 | 43 | 20.291
11.7 | 2.103 | 13 | 2.118 | 14.4 | 1.392 | 16 | 1.408 | 16.2 | 1.309 | 18 | 1.325 | 19.8 | 4.993 | 22 | 5.008 | 25.2 | 6.119 | 28 | 6.133 | 31.5 | 11.093 | 35 | 11.108 | 39.6 | 17.535 | 44 | 17.55
12.6 | 1.716 | 14 | 1.733 | 15.3 | 1.211 | 17 | 1.225 | 17.1 | 1.138 | 19 | 1.152 | 20.7 | 4.361 | 23 | 4.375 | 26.1 | 5.376 | 29 | 5.3913 | 32.4 | 9.718 | 36 | 9.733 | 40.5 | 15.404 | 45 | 15.418
13.5 | 1.442 | 15 | 1.458 | 16.2 | 1.062 | 18 | 1.077 | 18 | 0.999 | 20 | 1.016 | 21.6 | 3.852 | 24 | 3.866 | 27 | 4.777 | 30 | 4.7913 | 33.3 | 8.62 | 37 | 8.635 | 41.4 | 13.702 | 46 | 13.716
14.4 | 1.239 | 16 | 1.254 | 17.1 | 0.939 | 19 | 0.952 | 18.9 | 0.886 | 21 | 0.902 | 22.5 | 3.434 | 25 | 3.45 | 27.9 | 4.283 | 31 | 4.2997 | 34.2 | 7.723 | 38 | 7.737 | 42.3 | 12.312 | 47 | 12.327
15.3 | 1.082 | 17 | 1.096 | 18 | 0.834 | 20 | 0.85 | 19.8 | 0.793 | 22 | 0.808 | 23.4 | 3.086 | 26 | 3.1 | 28.8 | 3.87 | 32 | 3.8851 | 35.1 | 6.979 | 39 | 6.993 | 43.2 | 11.156 | 48 | 11.171
16.2 | 0.958 | 18 | 0.975 | 18.9 | 0.746 | 21 | 0.76 | 20.7 | 0.714 | 23 | 0.727 | 24.3 | 2.792 | 27 | 2.808 | 29.7 | 3.52 | 33 | 3.5351 | 36 | 6.35 | 40 | 6.366 | 44.1 | 10.181 | 49 | 10.193
17.1 | 0.857 | 19 | 0.871 | 19.8 | 0.671 | 22 | 0.685 | 21.6 | 0.647 | 24 | 0.66 | 25.2 | 2.541 | 28 | 2.558 | 30.6 | 3.22 | 34 | 3.2351 | 36.9 | 5.814 | 41 | 5.827 | 45 | 9.347 | 50 | 9.36
18 | 0.774 | 20 | 0.787 | 20.7 | 0.605 | 23 | 0.618 | 22.5 | 0.59 | 25 | 0.604 | 26.1 | 2.324 | 29 | 2.341 | 31.5 | 2.961 | 35 | 2.9747 | 37.8 | 5.351 | 42 | 5.366 | 45.9 | 8.626 | 51 | 8.641
18.9 | 0.704 | 21 | 0.718 | 21.6 | 0.552 | 24 | 0.566 | 23.4 | 0.54 | 26 | 0.554 | 27 | 2.136 | 30 | 2.15 | 32.4 | 2.734 | 36 | 2.7497 | 38.7 | 4.948 | 43 | 4.962 | 46.8 | 7.997 | 52 | 8.01
19.8 | 0.644 | 22 | 0.658 | 22.5 | 0.514 | 25 | 0.529 | 24.3 | 0.496 | 27 | 0.51 | 27.9 | 1.971 | 31 | 1.985 | 33.3 | 2.535 | 37 | 2.5497 | 39.6 | 4.593 | 44 | 4.608 | 47.7 | 7.444 | 53 | 7.458
20.7 | 0.593 | 23 | 0.608 | 23.4 | 0.48 | 26 | 0.493 | 25.2 | 0.458 | 28 | 0.475 | 28.8 | 1.826 | 32 | 1.841 | 34.2 | 2.358 | 38 | 2.3747 | 40.5 | 4.28 | 45 | 4.293 | 48.6 | 6.954 | 54 | 6.968
21.6 | 0.549 | 24 | 0.566 | 24.3 | 0.45 | 27 | 0.466 | 26.1 | 0.425 | 29 | 0.441 | 29.7 | 1.697 | 33 | 1.71 | 35.1 | 2.201 | 39 | 2.2163 | 41.4 | 4.001 | 46 | 4.016 | 49.5 | 6.517 | 55 | 6.533
22.5 | 0.51 | 25 | 0.525 | 25.2 | 0.422 | 28 | 0.435 | 27 | 0.395 | 30 | 0.408 | 30.6 | 1.582 | 34 | 1.596 | 36 | 2.06 | 40 | 2.0747 | 42.3 | 3.751 | 47 | 3.766 | 50.4 | 6.125 | 56 | 6.141
23.4 | 0.476 | 26 | 0.491 | 26.1 | 0.397 | 29 | 0.41 | 27.9 | 0.368 | 31 | 0.383 | 31.5 | 1.478 | 35 | 1.493 | 36.9 | 1.933 | 41 | 1.9497 | 43.2 | 3.526 | 48 | 3.541 | 51.3 | 5.772 | 57 | 5.785
24.3 | 0.446 | 27 | 0.46 | 27 | 0.374 | 30 | 0.391 | 28.8 | 0.344 | 32 | 0.358 | 32.4 | 1.385 | 36 | 1.4 | 37.8 | 1.819 | 42 | 1.833 | 44.1 | 3.323 | 49 | 3.337 | 52.2 | 5.452 | 58 | 5.466
25.2 | 0.419 | 28 | 0.433 | 27.9 | 0.354 | 31 | 0.368 | 29.7 | 0.322 | 33 | 0.337 | 33.3 | 1.301 | 37 | 1.316 | 38.7 | 1.714 | 43 | 1.7288 | 45 | 3.138 | 50 | 3.152 | 53.1 | 5.161 | 59 | 5.175
26.1 | 0.395 | 29 | 0.408 | 28.8 | 0.335 | 32 | 0.35 | 30.6 | 0.303 | 34 | 0.316 | 34.2 | 1.225 | 38 | 1.241 | 39.6 | 1.62 | 44 | 1.633 | 45.9 | 2.97 | 51 | 2.985 | 54 | 4.895 | 60 | 4.91
27 | 0.373 | 30 | 0.387 | 29.7 | 0.317 | 33 | 0.333 | 31.5 | 0.285 | 35 | 0.3 | 35.1 | 1.156 | 39 | 1.168 | 40.5 | 1.533 | 45 | 1.5497 | 46.8 | 2.816 | 52 | 2.833 | 54.9 | 4.652 | 61 | 4.666
27.9 | 0.353 | 31 | 0.366 | 30.6 | 0.301 | 34 | 0.316 | 32.4 | 0.269 | 36 | 0.283 | 36 | 1.092 | 40 | 1.108 | 41.4 | 1.453 | 46 | 1.4684 | 47.7 | 2.675 | 53 | 2.691 | 55.8 | 4.428 | 62 | 4.443
28.8 | 0.335 | 32 | 0.35 | 31.5 | 0.286 | 35 | 0.3 | 33.3 | 0.254 | 37 | 0.268 | 36.9 | 1.034 | 41 | 1.05 | 42.3 | 1.38 | 47 | 1.3934 | 48.6 | 2.545 | 54 | 2.558 | 56.7 | 4.222 | 63 | 4.235
29.7 | 0.318 | 33 | 0.333 | 32.4 | 0.272 | 36 | 0.285 | 34.2 | 0.241 | 38 | 0.258 | 37.8 | 0.98 | 42 | 0.993 | 43.2 | 1.313 | 48 | 1.3268 | 49.5 | 2.425 | 55 | 2.441 | 57.6 | 4.031 | 64 | 4.046
30.6 | 0.303 | 34 | 0.318 | 33.3 | 0.26 | 37 | 0.275 | 35.1 | 0.229 | 39 | 0.243 | 38.7 | 0.931 | 43 | 0.946 | 44.1 | 1.251 | 49 | 1.2663 | 50.4 | 2.314 | 56 | 2.327 | 58.5 | 3.854 | 65 | 3.868
31.5 | 0.289 | 35 | 0.304 | 34.2 | 0.248 | 38 | 0.262 | 36 | 0.217 | 40 | 0.233 | 39.6 | 0.885 | 44 | 0.9 | 45 | 1.193 | 50 | 1.208 | 51.3 | 2.211 | 57 | 2.225 | 59.4 | 3.69 | 66 | 3.704
32.4 | 0.276 | 36 | 0.291 | 35.1 | 0.237 | 39 | 0.252 | 36.9 | 0.207 | 41 | 0.221 | 40.5 | 0.843 | 45 | 0.858 | 45.9 | 1.139 | 51 | 1.1538 | 52.2 | 2.115 | 58 | 2.129 | 60.3 | 3.537 | 67 | 3.552
33.3 | 0.265 | 37 | 0.279 | 36 | 0.226 | 40 | 0.241 | 37.8 | 0.197 | 42 | 0.21 | 41.4 | 0.804 | 46 | 0.818 | 46.8 | 1.089 | 52 | 1.1038 | 53.1 | 2.025 | 59 | 2.041 | 61.2 | 3.394 | 68 | 3.408
34.2 | 0.254 | 38 | 0.268 | 36.9 | 0.217 | 41 | 0.233 | 38.7 | 0.188 | 43 | 0.202 | 42.3 | 0.768 | 47 | 0.783 | 47.7 | 1.043 | 53 | 1.058 | 54 | 1.942 | 60 | 1.958 | 62.1 | 3.26 | 69 | 3.275
35.1 | 0.244 | 39 | 0.258 | 37.8 | 0.208 | 42 | 0.225 | 39.6 | 0.179 | 44 | 0.194 | 43.2 | 0.734 | 48 | 0.75 | 48.6 | 0.999 | 54 | 1.0163 | 54.9 | 1.864 | 61 | 1.877 | 63 | 3.135 | 70 | 3.15
36 | 0.234 | 40 | 0.25 | 38.7 | 0.2 | 43 | 0.216 | 40.5 | 0.171 | 45 | 0.186 | 44.1 | 0.703 | 49 | 0.716 | 49.5 | 0.959 | 55 | 0.97467 | 55.8 | 1.791 | 62 | 1.808 | 63.9 | 3.017 | 71 | 3.033
36.9 | 0.225 | 41 | 0.241 | 39.6 | 0.192 | 44 | 0.208 | 41.4 | 0.164 | 46 | 0.182 | 45 | 0.673 | 50 | 0.687 | 50.4 | 0.921 | 56 | 0.93509 | 56.7 | 1.722 | 63 | 1.735 | 64.8 | 2.907 | 72 | 2.921
37.8 | 0.217 | 42 | 0.233 | 40.5 | 0.185 | 45 | 0.201 | 42.3 | 0.157 | 47 | 0.175 | 45.9 | 0.645 | 51 | 0.66 | 51.3 | 0.885 | 57 | 0.89967 | 57.6 | 1.658 | 64 | 1.675 | 65.7 | 2.803 | 73 | 2.816
38.7 | 0.209 | 43 | 0.225 | 41.4 | 0.179 | 46 | 0.194 | 43.2 | 0.151 | 48 | 0.166 | 46.8 | 0.619 | 52 | 0.633 | 52.2 | 0.851 | 58 | 0.86634 | 58.5 | 1.597 | 65 | 1.61 | 66.6 | 2.705 | 74 | 2.718
39.6 | 0.202 | 44 | 0.216 | 42.3 | 0.174 | 47 | 0.191 | 44.1 | 0.145 | 49 | 0.16 | 47.7 | 0.595 | 53 | 0.61 | 53.1 | 0.82 | 59 | 0.833 | 59.4 | 1.54 | 66 | 1.554 | 67.5 | 2.612 | 75 | 2.627
40.5 | 0.195 | 45 | 0.21 | 43.2 | 0.168 | 48 | 0.184 | 45 | 0.14 | 50 | 0.157 | 48.6 | 0.572 | 54 | 0.585 | 54 | 0.79 | 60 | 0.80384 | 60.3 | 1.486 | 67 | 1.5 | 68.4 | 2.524 | 76 | 2.541
41.4 | 0.188 | 46 | 0.202 | 44.1 | 0.164 | 49 | 0.177 | 45.9 | 0.134 | 51 | 0.15 | 49.5 | 0.551 | 55 | 0.566 | 54.9 | 0.761 | 61 | 0.77675 | 61.2 | 1.435 | 68 | 1.45 | 69.3 | 2.441 | 77 | 2.458
42.3 | 0.182 | 47 | 0.2 | 45 | 0.159 | 50 | 0.175 | 46.8 | 0.129 | 52 | 0.144 | 50.4 | 0.531 | 56 | 0.543 | 55.8 | 0.735 | 62 | 0.74967 | 62.1 | 1.386 | 69 | 1.4 | 70.2 | 2.363 | 78 | 2.377
43.2 | 0.177 | 48 | 0.193 | 45.9 | 0.154 | 51 | 0.169 | 47.7 | 0.125 | 53 | 0.141 | 51.3 | 0.511 | 57 | 0.525 | 56.7 | 0.71 | 63 | 0.72467 | 63 | 1.34 | 70 | 1.354 | 71.1 | 2.288 | 79 | 2.302
44.1 | 0.171 | 49 | 0.186 | 46.8 | 0.15 | 52 | 0.166 | 48.6 | 0.12 | 54 | 0.135 | 52.2 | 0.493 | 58 | 0.508 | 57.6 | 0.686 | 64 | 0.69967 | 63.9 | 1.297 | 71 | 1.31 | 72 | 2.217 | 80 | 2.233
45 | 0.166 | 50 | 0.183 | 47.7 | 0.146 | 53 | 0.161 | 49.5 | 0.116 | 55 | 0.133 | 53.1 | 0.476 | 59 | 0.491 | 58.5 | 0.663 | 65 | 0.67675 | 64.8 | 1.256 | 72 | 1.268 | 72.9 | 2.15 | 81 | 2.166
45.9 | 0.161 | 51 | 0.177 | 48.6 | 0.142 | 54 | 0.158 | 50.4 | 0.112 | 56 | 0.127 | 54 | 0.46 | 60 | 0.475 | 59.4 | 0.642 | 66 | 0.658 | 65.7 | 1.216 | 73 | 1.233 | 73.8 | 2.085 | 82 | 2.1
46.8 | 0.157 | 52 | 0.173 | 49.5 | 0.138 | 55 | 0.152 | 51.3 | 0.109 | 57 | 0.125 | 54.9 | 0.445 | 61 | 0.458 | 60.3 | 0.621 | 67 | 0.63509 | 66.6 | 1.179 | 74 | 1.193 | 74.7 | 2.024 | 83 | 2.041
47.7 | 0.152 | 53 | 0.168 | 50.4 | 0.135 | 56 | 0.151 | 52.2 | 0.105 | 58 | 0.119 | 55.8 | 0.43 | 62 | 0.443 | 61.2 | 0.602 | 68 | 0.61634 | 67.5 | 1.144 | 75 | 1.158 | 75.6 | 1.966 | 84 | 1.983
48.6 | 0.148 | 54 | 0.165 | 51.3 | 0.131 | 57 | 0.148 | 53.1 | 0.102 | 59 | 0.118 | 56.7 | 0.416 | 63 | 0.433 | 62.1 | 0.583 | 69 | 0.59967 | 68.4 | 1.11 | 76 | 1.125 | 76.5 | 1.91 | 85 | 1.925
49.5 | 0.144 | 55 | 0.159 | 52.2 | 0.128 | 58 | 0.143 | 54 | 0.099 | 60 | 0.116 | 57.6 | 0.403 | 64 | 0.416 | 63 | 0.566 | 70 | 0.583 | 69.3 | 1.077 | 77 | 1.091 | 77.4 | 1.857 | 86 | 1.871
50.4 | 0.14 | 56 | 0.158 | 53.1 | 0.125 | 59 | 0.141 | 54.9 | 0.096 | 61 | 0.111 | 58.5 | 0.39 | 65 | 0.404 | 63.9 | 0.549 | 71 | 0.56217 | 70.2 | 1.046 | 78 | 1.06 | 78.3 | 1.806 | 87 | 1.821
51.3 | 0.137 | 57 | 0.152 | 54 | 0.122 | 60 | 0.139 | 55.8 | 0.093 | 62 | 0.108 | 59.4 | 0.379 | 66 | 0.393 | 64.8 | 0.533 | 72 | 0.54967 | 71.1 | 1.017 | 79 | 1.033 | 79.2 | 1.757 | 88 | 1.771
52.2 | 0.133 | 58 | 0.15 | 54.9 | 0.119 | 61 | 0.134 | 56.7 | 0.09 | 63 | 0.108 | 60.3 | 0.367 | 67 | 0.383 | 65.7 | 0.518 | 73 | 0.533 | 72 | 0.989 | 80 | 1.002 | 80.1 | 1.711 | 89 | 1.725
53.1 | 0.13 | 59 | 0.144 | 55.8 | 0.116 | 62 | 0.133 | 57.6 | 0.088 | 64 | 0.102 | 61.2 | 0.356 | 68 | 0.371 | 66.6 | 0.503 | 74 | 0.51634 | 72.9 | 0.962 | 81 | 0.977 | 81 | 1.666 | 90 | 1.683
54 | 0.127 | 60 | 0.143 | 56.7 | 0.114 | 63 | 0.131 | 58.5 | 0.085 | 65 | 0.101 | 62.1 | 0.346 | 69 | 0.36 | 67.5 | 0.489 | 75 | 0.50175 | 73.8 | 0.936 | 82 | 0.95 | 81.9 | 1.623 | 91 | 1.637
54.9 | 0.124 | 61 | 0.141 | 57.6 | 0.111 | 64 | 0.126 | 59.4 | 0.083 | 66 | 0.1 | 63 | 0.336 | 70 | 0.35 | 68.4 | 0.476 | 76 | 0.49134 | 74.7 | 0.911 | 83 | 0.925 | 82.8 | 1.582 | 92 | 1.596
55.8 | 0.121 | 62 | 0.136 | 58.5 | 0.109 | 65 | 0.125 | 60.3 | 0.081 | 67 | 0.098 | 63.9 | 0.327 | 71 | 0.341 | 69.3 | 0.463 | 77 | 0.47675 | 75.6 | 0.887 | 84 | 0.902 | 83.7 | 1.542 | 93 | 1.558
56.7 | 0.118 | 63 | 0.134 | 59.4 | 0.106 | 66 | 0.123 | 61.2 | 0.079 | 68 | 0.093 | 64.8 | 0.317 | 72 | 0.333 | 70.2 | 0.45 | 78 | 0.46634 | 76.5 | 0.865 | 85 | 0.879 | 84.6 | 1.504 | 94 | 1.518
57.6 | 0.116 | 64 | 0.133 | 60.3 | 0.104 | 67 | 0.118 | 62.1 | 0.077 | 69 | 0.093 | 65.7 | 0.309 | 73 | 0.325 | 71.1 | 0.439 | 79 | 0.45175 | 77.4 | 0.843 | 86 | 0.858 | 85.5 | 1.468 | 95 | 1.483
58.5 | 0.113 | 65 | 0.127 | 61.2 | 0.102 | 68 | 0.118 | 63 | 0.075 | 70 | 0.091 | 66.6 | 0.301 | 74 | 0.316 | 72 | 0.427 | 80 | 0.44134 | 78.3 | 0.821 | 87 | 0.835 | 86.4 | 1.433 | 96 | 1.45
59.4 | 0.111 | 66 | 0.126 | 62.1 | 0.1 | 69 | 0.116 | 63.9 | 0.073 | 71 | 0.09 | 67.5 | 0.293 | 75 | 0.308 | 72.9 | 0.416 | 81 | 0.433 | 79.2 | 0.801 | 88 | 0.816 | 87.3 | 1.399 | 97 | 1.412
60.3 | 0.108 | 67 | 0.125 | 63 | 0.097 | 70 | 0.115 | 64.8 | 0.071 | 72 | 0.086 | 68.4 | 0.285 | 76 | 0.3 | 73.8 | 0.406 | 82 | 0.4205 | 80.1 | 0.782 | 89 | 0.796 | 88.2 | 1.366 | 98 | 1.383
61.2 | 0.106 | 68 | 0.123 | 63.9 | 0.096 | 71 | 0.11 | 65.7 | 0.069 | 73 | 0.084 | 69.3 | 0.278 | 77 | 0.291 | 74.7 | 0.396 | 83 | 0.41009 | 81 | 0.763 | 90 | 0.777 | 89.1 | 1.335 | 99 | 1.35
62.1 | 0.104 | 69 | 0.118 | 64.8 | 0.094 | 72 | 0.109 | 66.6 | 0.068 | 74 | 0.083 | 70.2 | 0.271 | 78 | 0.285 | 75.6 | 0.386 | 84 | 0.39967 | 81.9 | 0.745 | 91 | 0.76 | 90 | 1.304 | 100 | 1.318
63 | 0.102 | 70 | 0.118 | 65.7 | 0.092 | 73 | 0.108 | 67.5 | 0.066 | 75 | 0.083 | 71.1 | 0.264 | 79 | 0.277 | 76.5 | 0.377 | 85 | 0.39134 | 82.8 | 0.728 | 92 | 0.741 | 90.9 | 1.275 | 101 | 1.291
63.9 | 0.1 | 71 | 0.116 | 66.6 | 0.09 | 74 | 0.108 | 68.4 | 0.064 | 76 | 0.082 | 72 | 0.257 | 80 | 0.275 | 77.4 | 0.368 | 86 | 0.383 | 83.7 | 0.711 | 93 | 0.725 | 91.8 | 1.247 | 102 | 1.26
64.8 | 0.098 | 72 | 0.115 | 67.5 | 0.089 | 75 | 0.107 | 69.3 | 0.063 | 77 | 0.078 | 72.9 | 0.251 | 81 | 0.266 | 78.3 | 0.359 | 87 | 0.37467 | 84.6 | 0.695 | 94 | 0.708 | 92.7 | 1.22 | 103 | 1.235
65.7 | 0.096 | 73 | 0.111 | 68.4 | 0.087 | 76 | 0.102 | 70.2 | 0.062 | 78 | 0.077 | 73.8 | 0.245 | 82 | 0.26 | 79.2 | 0.351 | 88 | 0.36634 | 85.5 | 0.679 | 95 | 0.693 | 93.6 | 1.193 | 104 | 1.208
66.6 | 0.094 | 74 | 0.109 | 69.3 | 0.086 | 77 | 0.101 | 71.1 | 0.06 | 79 | 0.076 | 74.7 | 0.239 | 83 | 0.254 | 80.1 | 0.343 | 89 | 0.358 | 86.4 | 0.664 | 96 | 0.677 | 94.5 | 1.168 | 105 | 1.183
67.5 | 0.092 | 75 | 0.108 | 70.2 | 0.085 | 78 | 0.101 | 72 | 0.059 | 80 | 0.075 | 75.6 | 0.234 | 84 | 0.25 | 81 | 0.335 | 90 | 0.34967 | 87.3 | 0.649 | 97 | 0.666 | 95.4 | 1.143 | 106 | 1.158
68.4 | 0.091 | 76 | 0.108 | 71.1 | 0.083 | 79 | 0.1 | 72.9 | 0.058 | 81 | 0.075 | 76.5 | 0.228 | 85 | 0.243 | 81.9 | 0.328 | 91 | 0.34134 | 88.2 | 0.635 | 98 | 0.65 | 96.3 | 1.12 | 107 | 1.133
69.3 | 0.089 | 77 | 0.107 | 72 | 0.082 | 80 | 0.1 | 73.8 | 0.057 | 82 | 0.073 | 77.4 | 0.223 | 86 | 0.237 | 82.8 | 0.321 | 92 | 0.33509 | 89.1 | 0.622 | 99 | 0.635 | 97.2 | 1.097 | 108 | 1.11
70.2 | 0.087 | 78 | 0.102 | 72.9 | 0.081 | 81 | 0.098 | 74.7 | 0.055 | 83 | 0.069 | 78.3 | 0.218 | 87 | 0.233 | 83.7 | 0.314 | 93 | 0.32675 | 90 | 0.609 | 100 | 0.625 | 98.1 | 1.074 | 109 | 1.091
71.1 | 0.086 | 79 | 0.101 | 73.8 | 0.08 | 82 | 0.094 | 75.6 | 0.054 | 84 | 0.069 | 79.2 | 0.213 | 88 | 0.227 | 84.6 | 0.307 | 94 | 0.3205 | 90.9 | 0.596 | 101 | 0.61 | 99 | 1.053 | 110 | 1.066
72 | 0.084 | 80 | 0.1 | 74.7 | 0.079 | 83 | 0.093 | 76.5 | 0.053 | 85 | 0.068 | 80.1 | 0.209 | 89 | 0.225 | 85.5 | 0.301 | 95 | 0.31634 | 91.8 | 0.584 | 102 | 0.6 | 99.9 | 1.032 | 111 | 1.046
72.9 | 0.083 | 81 | 0.1 | 75.6 | 0.078 | 84 | 0.093 | 77.4 | 0.052 | 86 | 0.068 | 81 | 0.204 | 90 | 0.218 | 86.4 | 0.294 | 96 | 0.308 | 92.7 | 0.572 | 103 | 0.585 | 100.8 | 1.012 | 112 | 1.027
73.8 | 0.082 | 82 | 0.098 | 76.5 | 0.076 | 85 | 0.091 | 78.3 | 0.051 | 87 | 0.066 | 81.9 | 0.2 | 91 | 0.216 | 87.3 | 0.288 | 97 | 0.30175 | 93.6 | 0.56 | 104 | 0.575 | 101.7 | 0.992 | 113 | 1.008
74.7 | 0.08 | 83 | 0.094 | 77.4 | 0.075 | 86 | 0.091 | 79.2 | 0.05 | 88 | 0.066 | 82.8 | 0.196 | 92 | 0.21 | 88.2 | 0.282 | 98 | 0.29967 | 94.5 | 0.549 | 105 | 0.566 | 102.6 | 0.973 | 114 | 0.987
75.6 | 0.079 | 84 | 0.093 | 78.3 | 0.074 | 87 | 0.091 | 80.1 | 0.049 | 89 | 0.066 | 83.7 | 0.191 | 93 | 0.208 | 89.1 | 0.277 | 99 | 0.29134 | 95.4 | 0.538 | 106 | 0.552 | 103.5 | 0.954 | 115 | 0.968
76.5 | 0.078 | 85 | 0.093 | 79.2 | 0.073 | 88 | 0.09 | 81 | 0.048 | 90 | 0.065 | 84.6 | 0.187 | 94 | 0.202 | 90 | 0.271 | 100 | 0.28509 | 96.3 | 0.528 | 107 | 0.541 | 104.4 | 0.936 | 116 | 0.952
77.4 | 0.077 | 86 | 0.093 | 80.1 | 0.072 | 89 | 0.09 | 81.9 | 0.048 | 91 | 0.065 | 85.5 | 0.184 | 95 | 0.2 | 90.9 | 0.266 | 101 | 0.283 | 97.2 | 0.518 | 108 | 0.533 | 105.3 | 0.919 | 117 | 0.933
78.3 | 0.075 | 87 | 0.091 | 81 | 0.071 | 90 | 0.086 | 82.8 | 0.047 | 92 | 0.061 | 86.4 | 0.18 | 96 | 0.194 | 91.8 | 0.26 | 102 | 0.27467 | 98.1 | 0.508 | 109 | 0.525 | 106.2 | 0.902 | 118 | 0.916
79.2 | 0.074 | 88 | 0.091 | 81.9 | 0.07 | 91 | 0.085 | 83.7 | 0.046 | 93 | 0.061 | 87.3 | 0.176 | 97 | 0.191 | 92.7 | 0.255 | 103 | 0.26842 | 99 | 0.498 | 110 | 0.512 | 107.1 | 0.886 | 119 | 0.9
80.1 | 0.073 | 89 | 0.09 | 82.8 | 0.069 | 92 | 0.084 | 84.6 | 0.045 | 94 | 0.06 | 88.2 | 0.173 | 98 | 0.19 | 93.6 | 0.251 | 104 | 0.26634 | 99.9 | 0.489 | 111 | 0.502 | 108 | 0.87 | 120 | 0.883
81 | 0.072 | 90 | 0.086 | 83.7 | 0.069 | 93 | 0.084 | 85.5 | 0.044 | 95 | 0.06 | 89.1 | 0.169 | 99 | 0.184 | 94.5 | 0.246 | 105 | 0.26009 | 100.8 | 0.48 | 112 | 0.493 | 108.9 | 0.854 | 121 | 0.868
81.9 | 0.071 | 91 | 0.086 | 84.6 | 0.068 | 94 | 0.083 | 86.4 | 0.044 | 96 | 0.059 | 90 | 0.166 | 100 | 0.183 | 95.4 | 0.241 | 106 | 0.258 | 101.7 | 0.471 | 113 | 0.485 | 109.8 | 0.839 | 122 | 0.852
82.8 | 0.07 | 92 | 0.085 | 85.5 | 0.067 | 95 | 0.083 | 87.3 | 0.043 | 97 | 0.059 | 90.9 | 0.163 | 101 | 0.177 | 96.3 | 0.237 | 107 | 0.25175 | 102.6 | 0.462 | 114 | 0.477 | 110.7 | 0.824 | 123 | 0.841
83.7 | 0.069 | 93 | 0.084 | 86.4 | 0.066 | 96 | 0.083 | 88.2 | 0.042 | 98 | 0.058 | 91.8 | 0.16 | 102 | 0.176 | 97.2 | 0.232 | 108 | 0.24967 | 103.5 | 0.454 | 115 | 0.468 | 111.6 | 0.81 | 124 | 0.825
84.6 | 0.068 | 94 | 0.083 | 87.3 | 0.065 | 97 | 0.082 | 250.2 | 0.035 | 99 | 0.058 | 92.7 | 0.157 | 103 | 0.175 | 98.1 | 0.228 | 109 | 0.24342 | 104.4 | 0.446 | 116 | 0.46 | 112.5 | 0.796 | 125 | 0.81
85.5 | 0.067 | 95 | 0.083 | 88.2 | 0.064 | 98 | 0.082 | 250.2 | 0.007 | 100 | 0.058 | 93.6 | 0.154 | 104 | 0.169 | 99 | 0.224 | 110 | 0.24134 | 105.3 | 0.438 | 117 | 0.452 | 113.4 | 0.783 | 126 | 0.8
86.4 | 0.066 | 96 | 0.083 | 89.1 | 0.064 | 99 | 0.078 | 468 | 0.003 | 500 | 0.05 | 94.5 | 0.151 | 105 | 0.168 | 99.9 | 0.22 | 111 | 0.23509 | 106.2 | 0.431 | 118 | 0.443 | 114.3 | 0.769 | 127 | 0.783
87.3 | 0.065 | 97 | 0.082 | 90 | 0.063 | 100 | 0.078 | 6300 | 0.003 | 500 | 0.033 | 95.4 | 0.149 | 106 | 0.166 | 100.8 | 0.216 | 112 | 0.233 | 107.1 | 0.423 | 119 | 0.437 | 115.2 | 0.757 | 128 | 0.771
88.2 | 0.064 | 98 | 0.082 | 90.9 | 0.062 | 101 | 0.077 |  |  | 1000 | 0.033 | 96.3 | 0.146 | 107 | 0.161 | 101.7 | 0.213 | 113 | 0.22675 | 108 | 0.416 | 120 | 0.433 | 116.1 | 0.744 | 129 | 0.758
89.1 | 0.063 | 99 | 0.078 | 91.8 | 0.061 | 102 | 0.077 |  |  | 6300 | 0.022 | 97.2 | 0.143 | 108 | 0.159 | 102.6 | 0.209 | 114 | 0.22467 | 108.9 | 0.409 | 121 | 0.425 | 117 | 0.732 | 130 | 0.746
90 | 0.063 | 100 | 0.078 | 92.7 | 0.061 | 103 | 0.076 |  |  |  |  | 98.1 | 0.141 | 109 | 0.158 | 103.5 | 0.205 | 115 | 0.21842 | 109.8 | 0.402 | 122 | 0.416 | 117.9 | 0.72 | 131 | 0.735
90.9 | 0.062 | 101 | 0.077 | 93.6 | 0.06 | 104 | 0.075 |  |  |  |  | 99 | 0.139 | 110 | 0.152 | 104.4 | 0.202 | 116 | 0.21634 | 110.7 | 0.395 | 123 | 0.41 | 118.8 | 0.708 | 132 | 0.725
91.8 | 0.061 | 102 | 0.076 | 94.5 | 0.059 | 105 | 0.075 |  |  |  |  | 99.9 | 0.136 | 111 | 0.151 | 105.3 | 0.199 | 117 | 0.21217 | 111.6 | 0.389 | 124 | 0.402 | 119.7 | 0.697 | 133 | 0.71
92.7 | 0.06 | 103 | 0.076 | 95.4 | 0.058 | 106 | 0.075 |  |  |  |  | 100.8 | 0.134 | 112 | 0.15 | 106.2 | 0.195 | 118 | 0.21009 | 112.5 | 0.382 | 125 | 0.4 | 120.6 | 0.686 | 134 | 0.7
93.6 | 0.059 | 104 | 0.075 | 96.3 | 0.058 | 107 | 0.075 |  |  |  |  | 101.7 | 0.132 | 113 | 0.148 | 107.1 | 0.192 | 119 | 0.208 | 113.4 | 0.376 | 126 | 0.391 | 121.5 | 0.675 | 135 | 0.691
94.5 | 0.059 | 105 | 0.075 | 97.2 | 0.057 | 108 | 0.075 |  |  |  |  | 102.6 | 0.129 | 114 | 0.144 | 108 | 0.189 | 120 | 0.20245 | 114.3 | 0.37 | 127 | 0.385 | 122.4 | 0.665 | 136 | 0.679
95.4 | 0.058 | 106 | 0.075 | 98.1 | 0.056 | 109 | 0.073 |  |  |  |  | 103.5 | 0.127 | 115 | 0.143 | 108.9 | 0.186 | 121 | 0.20106 | 115.2 | 0.364 | 128 | 0.379 | 123.3 | 0.655 | 137 | 0.668
96.3 | 0.057 | 107 | 0.075 | 99 | 0.056 | 110 | 0.073 |  |  |  |  | 104.4 | 0.125 | 116 | 0.141 | 109.8 | 0.183 | 122 | 0.19967 | 116.1 | 0.359 | 129 | 0.375 | 124.2 | 0.645 | 138 | 0.658
97.2 | 0.057 | 108 | 0.073 | 99.9 | 0.055 | 111 | 0.069 |  |  |  |  | 105.3 | 0.123 | 117 | 0.14 | 110.7 | 0.18 | 123 | 0.19411 | 117 | 0.353 | 130 | 0.366 | 125.1 | 0.635 | 139 | 0.65
98.1 | 0.056 | 109 | 0.073 | 100.8 | 0.055 | 112 | 0.069 |  |  |  |  | 106.2 | 0.121 | 118 | 0.136 | 111.6 | 0.177 | 124 | 0.19273 | 117.9 | 0.348 | 131 | 0.362 | 126 | 0.625 | 140 | 0.641
99 | 0.055 | 110 | 0.069 | 101.7 | 0.054 | 113 | 0.068 |  |  |  |  | 107.1 | 0.119 | 119 | 0.134 | 112.5 | 0.174 | 125 | 0.19134 | 118.8 | 0.342 | 132 | 0.358 | 126.9 | 0.616 | 141 | 0.633
99.9 | 0.055 | 111 | 0.069 | 102.6 | 0.053 | 114 | 0.068 |  |  |  |  | 108 | 0.118 | 120 | 0.133 | 113.4 | 0.172 | 126 | 0.18578 | 119.7 | 0.337 | 133 | 0.352 | 127.8 | 0.607 | 142 | 0.621
100.8 | 0.054 | 112 | 0.068 | 103.5 | 0.053 | 115 | 0.068 |  |  |  |  | 108.9 | 0.116 | 121 | 0.133 | 114.3 | 0.169 | 127 | 0.18439 | 120.6 | 0.332 | 134 | 0.346 | 128.7 | 0.598 | 143 | 0.612
101.7 | 0.053 | 113 | 0.068 | 104.4 | 0.052 | 116 | 0.068 |  |  |  |  | 109.8 | 0.114 | 122 | 0.132 | 115.2 | 0.166 | 128 | 0.183 | 121.5 | 0.327 | 135 | 0.341 | 129.6 | 0.589 | 144 | 0.604
102.6 | 0.053 | 114 | 0.068 | 105.3 | 0.052 | 117 | 0.068 |  |  |  |  | 110.7 | 0.112 | 123 | 0.127 | 116.1 | 0.164 | 129 | 0.18161 | 122.4 | 0.322 | 136 | 0.335 | 130.5 | 0.581 | 145 | 0.596
103.5 | 0.052 | 115 | 0.068 | 106.2 | 0.051 | 118 | 0.066 |  |  |  |  | 111.6 | 0.111 | 124 | 0.126 | 117 | 0.161 | 130 | 0.17675 | 123.3 | 0.317 | 137 | 0.333 | 131.4 | 0.573 | 146 | 0.587
104.4 | 0.052 | 116 | 0.068 | 107.1 | 0.051 | 119 | 0.066 |  |  |  |  | 112.5 | 0.109 | 125 | 0.125 | 117.9 | 0.159 | 131 | 0.17467 | 124.2 | 0.313 | 138 | 0.327 | 132.3 | 0.564 | 147 | 0.579
105.3 | 0.051 | 117 | 0.066 | 108 | 0.05 | 120 | 0.066 |  |  |  |  | 113.4 | 0.107 | 126 | 0.125 | 118.8 | 0.157 | 132 | 0.17328 | 125.1 | 0.308 | 139 | 0.325 | 133.2 | 0.556 | 148 | 0.571
106.2 | 0.051 | 118 | 0.066 | 108.9 | 0.05 | 121 | 0.066 |  |  |  |  | 114.3 | 0.106 | 127 | 0.123 | 119.7 | 0.155 | 133 | 0.16911 | 126 | 0.304 | 140 | 0.318 | 134.1 | 0.549 | 149 | 0.562
107.1 | 0.05 | 119 | 0.066 | 109.8 | 0.049 | 122 | 0.066 |  |  |  |  | 115.2 | 0.104 | 128 | 0.119 | 120.6 | 0.152 | 134 | 0.16773 | 126.9 | 0.3 | 141 | 0.316 | 135 | 0.541 | 150 | 0.558
108 | 0.049 | 120 | 0.066 | 110.7 | 0.049 | 123 | 0.066 |  |  |  |  | 116.1 | 0.103 | 129 | 0.118 | 121.5 | 0.15 | 135 | 0.16634 | 127.8 | 0.295 | 142 | 0.31 | 135.9 | 0.534 | 151 | 0.55
108.9 | 0.049 | 121 | 0.066 | 111.6 | 0.048 | 124 | 0.065 |  |  |  |  | 117 | 0.101 | 130 | 0.118 | 122.4 | 0.148 | 136 | 0.16495 | 128.7 | 0.291 | 143 | 0.308 | 136.8 | 0.526 | 152 | 0.541
109.8 | 0.048 | 122 | 0.065 | 112.5 | 0.048 | 125 | 0.065 |  |  |  |  | 117.9 | 0.1 | 131 | 0.116 | 123.3 | 0.146 | 137 | 0.16078 | 129.6 | 0.287 | 144 | 0.302 | 137.7 | 0.519 | 153 | 0.533
110.7 | 0.048 | 123 | 0.065 | 113.4 | 0.047 | 126 | 0.065 |  |  |  |  | 118.8 | 0.099 | 132 | 0.115 | 124.2 | 0.144 | 138 | 0.15939 | 130.5 | 0.283 | 145 | 0.3 | 138.6 | 0.512 | 154 | 0.527
111.6 | 0.047 | 124 | 0.065 | 114.3 | 0.047 | 127 | 0.061 |  |  |  |  | 119.7 | 0.097 | 133 | 0.115 | 125.1 | 0.142 | 139 | 0.158 | 131.4 | 0.279 | 146 | 0.293 | 139.5 | 0.505 | 155 | 0.518
112.5 | 0.047 | 125 | 0.064 | 115.2 | 0.046 | 128 | 0.061 |  |  |  |  | 120.6 | 0.096 | 134 | 0.111 | 126 | 0.14 | 140 | 0.15661 | 132.3 | 0.276 | 147 | 0.291 | 140.4 | 0.499 | 156 | 0.512
113.4 | 0.047 | 126 | 0.061 | 116.1 | 0.046 | 129 | 0.061 |  |  |  |  | 121.5 | 0.095 | 135 | 0.11 | 126.9 | 0.138 | 141 | 0.15245 | 133.2 | 0.272 | 148 | 0.285 | 141.3 | 0.492 | 157 | 0.508
114.3 | 0.046 | 127 | 0.061 | 117 | 0.045 | 130 | 0.06 |  |  |  |  | 122.4 | 0.093 | 136 | 0.109 | 127.8 | 0.136 | 142 | 0.15175 | 134.1 | 0.268 | 149 | 0.283 | 142.2 | 0.486 | 158 | 0.5
115.2 | 0.046 | 128 | 0.061 | 117.9 | 0.045 | 131 | 0.06 |  |  |  |  | 123.3 | 0.092 | 137 | 0.108 | 128.7 | 0.135 | 143 | 0.14967 | 135 | 0.265 | 150 | 0.279 | 143.1 | 0.479 | 159 | 0.493
116.1 | 0.045 | 129 | 0.06 | 118.8 | 0.045 | 132 | 0.06 |  |  |  |  | 124.2 | 0.091 | 138 | 0.108 | 129.6 | 0.133 | 144 | 0.14967 | 135.9 | 0.261 | 151 | 0.275 | 144 | 0.473 | 160 | 0.487
117 | 0.045 | 130 | 0.06 | 119.7 | 0.044 | 133 | 0.059 |  |  |  |  | 125.1 | 0.09 | 139 | 0.107 | 130.5 | 0.131 | 145 | 0.14828 | 136.8 | 0.258 | 152 | 0.275 | 144.9 | 0.467 | 161 | 0.483
117.9 | 0.044 | 131 | 0.059 | 120.6 | 0.044 | 134 | 0.059 |  |  |  |  | 126 | 0.089 | 140 | 0.102 | 131.4 | 0.129 | 146 | 0.14412 | 137.7 | 0.254 | 153 | 0.268 | 145.8 | 0.461 | 162 | 0.475
118.8 | 0.044 | 132 | 0.059 | 121.5 | 0.043 | 135 | 0.059 |  |  |  |  | 126.9 | 0.087 | 141 | 0.102 | 132.3 | 0.128 | 147 | 0.14273 | 138.6 | 0.251 | 154 | 0.266 | 146.7 | 0.455 | 163 | 0.468
119.7 | 0.044 | 133 | 0.059 | 122.4 | 0.043 | 136 | 0.058 |  |  |  |  | 127.8 | 0.086 | 142 | 0.102 | 133.2 | 0.126 | 148 | 0.14134 | 139.5 | 0.248 | 155 | 0.262 | 147.6 | 0.45 | 164 | 0.466
120.6 | 0.043 | 134 | 0.059 | 123.3 | 0.043 | 500 | 0.05 |  |  |  |  | 128.7 | 0.085 | 143 | 0.101 | 134.1 | 0.124 | 149 | 0.14134 | 140.4 | 0.245 | 156 | 0.26 | 148.5 | 0.444 | 165 | 0.458
121.5 | 0.043 | 135 | 0.058 | 124.2 | 0.042 | 500 | 0.033 |  |  |  |  | 129.6 | 0.084 | 144 | 0.1 | 135 | 0.123 | 150 | 0.13995 | 141.3 | 0.242 | 157 | 0.258 | 149.4 | 0.439 | 166 | 0.452
122.4 | 0.042 | 500 | 0.05 | 125.1 | 0.042 | 1000 | 0.033 |  |  |  |  | 130.5 | 0.083 | 145 | 0.1 | 135.9 | 0.121 | 151 | 0.13578 | 142.2 | 0.239 | 158 | 0.252 | 150.3 | 0.433 | 167 | 0.45
250.2 | 0.036 | 500 | 0.033 | 126 | 0.041 | 6300 | 0.022 |  |  |  |  | 131.4 | 0.082 | 146 | 0.1 | 136.8 | 0.12 | 152 | 0.13508 | 143.1 | 0.236 | 159 | 0.25 | 151.2 | 0.428 | 168 | 0.441
250.2 | 0.007 | 1000 | 0.033 | 250.2 | 0.036 | [6 empty] | 132.3 | 0.081 | 147 | 0.098 | 137.7 | 0.118 | 153 | 0.13439 | 144 | 0.233 | 160 | 0.25 | 152.1 | 0.423 | 169 | 0.437
468 | 0.003 | 6300 | 0.022 | 250.2 | 0.007 | [6 empty] | 133.2 | 0.08 | 148 | 0.094 | 138.6 | 0.117 | 154 | 0.133 | 144.9 | 0.23 | 161 | 0.243 | 153 | 0.418 | 170 | 0.433
6300 | 0.003 |  |  | 468 | 0.003 | [6 empty] | 134.1 | 0.079 | 149 | 0.094 | 139.5 | 0.116 | 155 | 0.133 | 145.8 | 0.227 | 162 | 0.241 | 153.9 | 0.413 | 171 | 0.427
|  |  |  | 6300 | 0.003 | [6 empty] | 135 | 0.078 | 150 | 0.093 | 140.4 | 0.114 | 156 | 0.13162 | 146.7 | 0.224 | 163 | 0.241 | 154.8 | 0.408 | 172 | 0.425
[12 empty] | 135.9 | 0.077 | 151 | 0.093 | 141.3 | 0.113 | 157 | 0.12745 | 147.6 | 0.222 | 164 | 0.235 | 155.7 | 0.403 | 173 | 0.418
[12 empty] | 136.8 | 0.076 | 152 | 0.093 | 142.2 | 0.111 | 158 | 0.12676 | 148.5 | 0.219 | 165 | 0.233 | 156.6 | 0.398 | 174 | 0.412
[12 empty] | 137.7 | 0.076 | 153 | 0.091 | 143.1 | 0.11 | 159 | 0.12606 | 149.4 | 0.217 | 166 | 0.233 | 157.5 | 0.394 | 175 | 0.408
[12 empty] | 138.6 | 0.075 | 154 | 0.091 | 144 | 0.109 | 160 | 0.12467 | 150.3 | 0.214 | 167 | 0.227 | 158.4 | 0.389 | 176 | 0.404
[12 empty] | 139.5 | 0.074 | 155 | 0.091 | 144.9 | 0.108 | 161 | 0.12467 | 151.2 | 0.212 | 168 | 0.227 | 159.3 | 0.385 | 177 | 0.4
[12 empty] | 140.4 | 0.073 | 156 | 0.09 | 145.8 | 0.106 | 162 | 0.12328 | 152.1 | 0.209 | 169 | 0.225 | 160.2 | 0.38 | 178 | 0.393
[12 empty] | 141.3 | 0.072 | 157 | 0.089 | 146.7 | 0.105 | 163 | 0.11911 | 153 | 0.207 | 170 | 0.221 | 161.1 | 0.376 | 179 | 0.391
[12 empty] | 142.2 | 0.071 | 158 | 0.086 | 147.6 | 0.104 | 164 | 0.11841 | 153.9 | 0.204 | 171 | 0.218 | 162 | 0.372 | 180 | 0.385
[12 empty] | 143.1 | 0.071 | 159 | 0.085 | 148.5 | 0.103 | 165 | 0.11841 | 154.8 | 0.202 | 172 | 0.216 | 162.9 | 0.368 | 181 | 0.383
[12 empty] | 144 | 0.07 | 160 | 0.085 | 149.4 | 0.102 | 166 | 0.11772 | 155.7 | 0.2 | 173 | 0.216 | 163.8 | 0.364 | 182 | 0.377
[12 empty] | 144.9 | 0.069 | 161 | 0.084 | 150.3 | 0.101 | 167 | 0.11634 | 156.6 | 0.197 | 174 | 0.212 | 164.7 | 0.36 | 183 | 0.375
[12 empty] | 145.8 | 0.068 | 162 | 0.084 | 151.2 | 0.1 | 168 | 0.11634 | 157.5 | 0.195 | 175 | 0.21 | 165.6 | 0.356 | 184 | 0.368
[12 empty] | 146.7 | 0.068 | 163 | 0.083 | 152.1 | 0.098 | 169 | 0.11496 | 158.4 | 0.193 | 176 | 0.208 | 166.5 | 0.352 | 185 | 0.366
[12 empty] | 147.6 | 0.067 | 164 | 0.083 | 153 | 0.097 | 170 | 0.11496 | 159.3 | 0.191 | 177 | 0.208 | 167.4 | 0.348 | 186 | 0.362
[12 empty] | 148.5 | 0.066 | 165 | 0.083 | 153.9 | 0.096 | 171 | 0.11079 | 160.2 | 0.189 | 178 | 0.202 | 168.3 | 0.344 | 187 | 0.358
[12 empty] | 149.4 | 0.065 | 166 | 0.083 | 154.8 | 0.095 | 172 | 0.1101 | 161.1 | 0.187 | 179 | 0.202 | 169.2 | 0.341 | 188 | 0.358
[12 empty] | 150.3 | 0.065 | 167 | 0.082 | 155.7 | 0.094 | 173 | 0.1094 | 162 | 0.185 | 180 | 0.2 | 170.1 | 0.337 | 189 | 0.352
[12 empty] | 151.2 | 0.064 | 168 | 0.082 | 156.6 | 0.093 | 174 | 0.1094 | 162.9 | 0.183 | 181 | 0.2 | 171 | 0.333 | 190 | 0.35
[12 empty] | 152.1 | 0.063 | 169 | 0.078 | 157.5 | 0.092 | 175 | 0.108 | 163.8 | 0.181 | 182 | 0.198 | 171.9 | 0.33 | 191 | 0.343
[12 empty] | 153 | 0.063 | 170 | 0.078 | 158.4 | 0.091 | 176 | 0.108 | 164.7 | 0.179 | 183 | 0.193 | 172.8 | 0.326 | 192 | 0.341
[12 empty] | 153.9 | 0.062 | 171 | 0.077 | 159.3 | 0.09 | 177 | 0.108 | 165.6 | 0.177 | 184 | 0.193 | 173.7 | 0.323 | 193 | 0.337
[12 empty] | 154.8 | 0.062 | 172 | 0.077 | 160.2 | 0.09 | 178 | 0.1066 | 166.5 | 0.175 | 185 | 0.191 | 174.6 | 0.32 | 194 | 0.333
[12 empty] | 155.7 | 0.061 | 173 | 0.076 | 161.1 | 0.089 | 179 | 0.10243 | 167.4 | 0.173 | 186 | 0.19 | 175.5 | 0.316 | 195 | 0.333
[12 empty] | 156.6 | 0.06 | 174 | 0.076 | 162 | 0.088 | 180 | 0.10243 | 168.3 | 0.171 | 187 | 0.186 | 176.4 | 0.313 | 196 | 0.327
[12 empty] | 157.5 | 0.06 | 175 | 0.076 | 162.9 | 0.087 | 181 | 0.10174 | 169.2 | 0.17 | 188 | 0.185 | 177.3 | 0.31 | 197 | 0.325
[12 empty] | 158.4 | 0.059 | 176 | 0.075 | 163.8 | 0.086 | 182 | 0.10105 | 170.1 | 0.168 | 189 | 0.183 | 178.2 | 0.307 | 198 | 0.321
[12 empty] | 159.3 | 0.059 | 177 | 0.075 | 164.7 | 0.085 | 183 | 0.10105 | 171 | 0.166 | 190 | 0.183 | 179.1 | 0.304 | 199 | 0.318
[12 empty] | 160.2 | 0.058 | 178 | 0.075 | 165.6 | 0.084 | 184 | 0.099673 | 171.9 | 0.165 | 191 | 0.182 | 180 | 0.301 | 200 | 0.316
[12 empty] | 161.1 | 0.058 | 179 | 0.075 | 166.5 | 0.083 | 185 | 0.099673 | 172.8 | 0.163 | 192 | 0.177 | 180.9 | 0.298 | 201 | 0.312
[12 empty] | 162 | 0.057 | 180 | 0.075 | 167.4 | 0.083 | 186 | 0.099673 | 173.7 | 0.161 | 193 | 0.177 | 181.8 | 0.295 | 202 | 0.31
[12 empty] | 162.9 | 0.056 | 181 | 0.073 | 168.3 | 0.082 | 187 | 0.098297 | 174.6 | 0.16 | 194 | 0.176 | 182.7 | 0.292 | 203 | 0.308
[12 empty] | 163.8 | 0.056 | 182 | 0.073 | 169.2 | 0.081 | 188 | 0.098297 | 175.5 | 0.158 | 195 | 0.175 | 183.6 | 0.289 | 204 | 0.302
[12 empty] | 164.7 | 0.055 | 183 | 0.069 | 170.1 | 0.08 | 189 | 0.09414 | 176.4 | 0.157 | 196 | 0.173 | 184.5 | 0.286 | 205 | 0.3
[12 empty] | 165.6 | 0.055 | 184 | 0.069 | 171 | 0.08 | 190 | 0.09414 | 177.3 | 0.155 | 197 | 0.169 | 185.4 | 0.283 | 206 | 0.3
[12 empty] | 166.5 | 0.054 | 185 | 0.069 | 171.9 | 0.079 | 191 | 0.09344 | 178.2 | 0.154 | 198 | 0.168 | 186.3 | 0.281 | 207 | 0.293
[12 empty] | 167.4 | 0.054 | 186 | 0.068 | 172.8 | 0.078 | 192 | 0.09344 | 179.1 | 0.152 | 199 | 0.168 | 187.2 | 0.278 | 208 | 0.291
[12 empty] | 168.3 | 0.053 | 187 | 0.068 | 173.7 | 0.077 | 193 | 0.092739 | 180 | 0.151 | 200 | 0.166 | 188.1 | 0.275 | 209 | 0.291
[12 empty] | 169.2 | 0.053 | 188 | 0.068 | 174.6 | 0.077 | 194 | 0.092739 | 180.9 | 0.149 | 201 | 0.166 | 189 | 0.273 | 210 | 0.287
[12 empty] | 170.1 | 0.052 | 189 | 0.068 | 175.5 | 0.076 | 195 | 0.091332 | 181.8 | 0.148 | 202 | 0.165 | 189.9 | 0.27 | 211 | 0.285
[12 empty] | 171 | 0.052 | 190 | 0.068 | 176.4 | 0.075 | 196 | 0.091333 | 182.7 | 0.146 | 203 | 0.161 | 190.8 | 0.268 | 212 | 0.283
[12 empty] | 171.9 | 0.052 | 191 | 0.068 | 177.3 | 0.075 | 197 | 0.091333 | 183.6 | 0.145 | 204 | 0.16 | 191.7 | 0.265 | 213 | 0.279
[12 empty] | 172.8 | 0.051 | 192 | 0.066 | 178.2 | 0.074 | 198 | 0.091332 | 184.5 | 0.144 | 205 | 0.159 | 192.6 | 0.263 | 214 | 0.277
[12 empty] | 173.7 | 0.051 | 193 | 0.066 | 179.1 | 0.073 | 199 | 0.089925 | 185.4 | 0.142 | 206 | 0.158 | 193.5 | 0.26 | 215 | 0.275
[12 empty] | 174.6 | 0.05 | 194 | 0.066 | 180 | 0.073 | 200 | 0.089925 | 186.3 | 0.141 | 207 | 0.158 | 194.4 | 0.258 | 216 | 0.275
[12 empty] | 175.5 | 0.05 | 195 | 0.066 | 180.9 | 0.072 | 201 | 0.085744 | 187.2 | 0.14 | 208 | 0.157 | 195.3 | 0.256 | 217 | 0.268
[12 empty] | 176.4 | 0.049 | 196 | 0.066 | 181.8 | 0.071 | 202 | 0.085744 | 188.1 | 0.139 | 209 | 0.152 | 196.2 | 0.253 | 218 | 0.268
[12 empty] | 177.3 | 0.049 | 197 | 0.066 | 182.7 | 0.071 | 203 | 0.085057 | 189 | 0.137 | 210 | 0.152 | 197.1 | 0.251 | 219 | 0.266
[12 empty] | 178.2 | 0.049 | 198 | 0.066 | 183.6 | 0.07 | 204 | 0.085057 | 189.9 | 0.136 | 211 | 0.151 | 198 | 0.249 | 220 | 0.262
[12 empty] | 179.1 | 0.048 | 199 | 0.065 | 184.5 | 0.07 | 205 | 0.085057 | 190.8 | 0.135 | 212 | 0.151 | 198.9 | 0.247 | 221 | 0.26
[12 empty] | 180 | 0.048 | 200 | 0.065 | 185.4 | 0.069 | 206 | 0.084373 | 191.7 | 0.134 | 213 | 0.15 | 199.8 | 0.244 | 222 | 0.258
[12 empty] | 180.9 | 0.047 | 201 | 0.065 | 186.3 | 0.068 | 207 | 0.084373 | 192.6 | 0.132 | 214 | 0.15 | 200.7 | 0.242 | 223 | 0.258
[12 empty] | 181.8 | 0.047 | 202 | 0.064 | 187.2 | 0.068 | 208 | 0.08301 | 193.5 | 0.131 | 215 | 0.148 | 201.6 | 0.24 | 224 | 0.254
[12 empty] | 182.7 | 0.047 | 203 | 0.061 | 188.1 | 0.067 | 209 | 0.08301 | 194.4 | 0.13 | 216 | 0.144 | 202.5 | 0.238 | 225 | 0.252
[12 empty] | 183.6 | 0.046 | 204 | 0.061 | 189 | 0.067 | 210 | 0.08301 | 195.3 | 0.129 | 217 | 0.143 | 203.4 | 0.236 | 226 | 0.25
[12 empty] | 184.5 | 0.046 | 205 | 0.061 | 189.9 | 0.066 | 211 | 0.08301 | 196.2 | 0.128 | 218 | 0.143 | 204.3 | 0.234 | 227 | 0.25
[12 empty] | 185.4 | 0.046 | 206 | 0.061 | 190.8 | 0.066 | 212 | 0.08301 | 197.1 | 0.127 | 219 | 0.143 | 205.2 | 0.232 | 228 | 0.246
[12 empty] | 186.3 | 0.045 | 207 | 0.06 | 191.7 | 0.065 | 213 | 0.081649 | 198 | 0.126 | 220 | 0.141 | 206.1 | 0.23 | 229 | 0.243
[12 empty] | 187.2 | 0.045 | 208 | 0.06 | 192.6 | 0.065 | 214 | 0.081649 | 198.9 | 0.125 | 221 | 0.141 | 207 | 0.228 | 230 | 0.241
[12 empty] | 188.1 | 0.045 | 209 | 0.06 | 193.5 | 0.064 | 215 | 0.081649 | 199.8 | 0.124 | 222 | 0.14 | 207.9 | 0.226 | 231 | 0.241
[12 empty] | 189 | 0.044 | 210 | 0.059 | 194.4 | 0.063 | 216 | 0.077503 | 200.7 | 0.123 | 223 | 0.14 | 208.8 | 0.224 | 232 | 0.241
[12 empty] | 189.9 | 0.044 | 211 | 0.059 | 195.3 | 0.063 | 217 | 0.077503 | 201.6 | 0.121 | 224 | 0.136 | 209.7 | 0.222 | 233 | 0.235
[12 empty] | 190.8 | 0.044 | 212 | 0.059 | 196.2 | 0.062 | 218 | 0.077503 | 202.5 | 0.12 | 225 | 0.135 | 210.6 | 0.22 | 234 | 0.235
[12 empty] | 191.7 | 0.043 | 213 | 0.059 | 197.1 | 0.062 | 219 | 0.076797 | 203.4 | 0.119 | 226 | 0.134 | 211.5 | 0.218 | 235 | 0.233
[12 empty] | 192.6 | 0.043 | 214 | 0.058 | 198 | 0.062 | 220 | 0.076797 | 204.3 | 0.118 | 227 | 0.134 | 212.4 | 0.217 | 236 | 0.233
[12 empty] | 193.5 | 0.043 | 500 | 0.05 | 198.9 | 0.061 | 221 | 0.076088 | 205.2 | 0.118 | 228 | 0.133 | 213.3 | 0.215 | 237 | 0.229
[12 empty] | 194.4 | 0.042 | 500 | 0.033 | 199.8 | 0.061 | 222 | 0.076088 | 206.1 | 0.117 | 229 | 0.133 | 214.2 | 0.213 | 238 | 0.227
[12 empty] | 250.2 | 0.04 | 1000 | 0.033 | 200.7 | 0.06 | 223 | 0.076088 | 207 | 0.116 | 230 | 0.133 | 215.1 | 0.211 | 239 | 0.225
[12 empty] | 250.2 | 0.007 | 6300 | 0.022 | 201.6 | 0.06 | 224 | 0.076088 | 207.9 | 0.115 | 231 | 0.132 | 216 | 0.21 | 240 | 0.225
[12 empty] | 468 | 0.003 |  |  | 202.5 | 0.059 | 225 | 0.07466 | 208.8 | 0.114 | 232 | 0.131 | 216.9 | 0.208 | 241 | 0.225
[12 empty] | 6300 | 0.003 |  |  | 203.4 | 0.059 | 226 | 0.074661 | 209.7 | 0.113 | 233 | 0.127 | 217.8 | 0.206 | 242 | 0.221
[16 empty] | 204.3 | 0.058 | 227 | 0.07466 | 210.6 | 0.112 | 234 | 0.127 | 218.7 | 0.205 | 243 | 0.218
[16 empty] | 205.2 | 0.058 | 228 | 0.074661 | 211.5 | 0.111 | 235 | 0.126 | 219.6 | 0.203 | 244 | 0.216
[16 empty] | 206.1 | 0.057 | 229 | 0.074661 | 212.4 | 0.11 | 236 | 0.126 | 220.5 | 0.201 | 245 | 0.216
[16 empty] | 207 | 0.057 | 230 | 0.07466 | 213.3 | 0.109 | 237 | 0.125 | 221.4 | 0.2 | 246 | 0.216
[16 empty] | 207.9 | 0.057 | 231 | 0.073231 | 214.2 | 0.108 | 238 | 0.125 | 222.3 | 0.198 | 247 | 0.212
[16 empty] | 208.8 | 0.056 | 232 | 0.073231 | 215.1 | 0.108 | 239 | 0.125 | 223.2 | 0.197 | 248 | 0.21
[16 empty] | 209.7 | 0.056 | 233 | 0.07323 | 216 | 0.107 | 240 | 0.123 | 224.1 | 0.195 | 249 | 0.21
[16 empty] | 210.6 | 0.055 | 234 | 0.069033 | 216.9 | 0.106 | 241 | 0.123 | 225 | 0.193 | 250 | 0.209
[16 empty] | 211.5 | 0.055 | 235 | 0.069033 | 217.8 | 0.105 | 242 | 0.119 | 225.9 | 0.192 | 251 | 0.208
[16 empty] | 212.4 | 0.055 | 236 | 0.069033 | 218.7 | 0.104 | 243 | 0.119 | 226.8 | 0.19 | 252 | 0.208
[16 empty] | 213.3 | 0.054 | 237 | 0.069033 | 219.6 | 0.104 | 244 | 0.118 | 227.7 | 0.189 | 253 | 0.206
[16 empty] | 214.2 | 0.054 | 238 | 0.068355 | 220.5 | 0.103 | 245 | 0.118 | 228.6 | 0.187 | 254 | 0.202
[16 empty] | 215.1 | 0.053 | 239 | 0.068355 | 221.4 | 0.102 | 246 | 0.118 | 229.5 | 0.186 | 255 | 0.201
[16 empty] | 216 | 0.053 | 240 | 0.068355 | 222.3 | 0.101 | 247 | 0.116 | 230.4 | 0.185 | 256 | 0.2
[16 empty] | 216.9 | 0.053 | 241 | 0.067683 | 223.2 | 0.101 | 248 | 0.116 | 231.3 | 0.183 | 257 | 0.2
[16 empty] | 217.8 | 0.052 | 242 | 0.067683 | 224.1 | 0.1 | 249 | 0.116 | 232.2 | 0.182 | 258 | 0.198
[16 empty] | 218.7 | 0.052 | 243 | 0.067683 | 225 | 0.099 | 250 | 0.116 | 233.1 | 0.18 | 259 | 0.198
[16 empty] | 219.6 | 0.052 | 244 | 0.067683 | 225.9 | 0.098 | 251 | 0.115 | 234 | 0.179 | 260 | 0.194
[16 empty] | 220.5 | 0.051 | 245 | 0.066351 | 226.8 | 0.098 | 252 | 0.115 | 234.9 | 0.178 | 261 | 0.193
[16 empty] | 221.4 | 0.051 | 246 | 0.066351 | 227.7 | 0.097 | 253 | 0.111 | 235.8 | 0.176 | 262 | 0.193
[16 empty] | 222.3 | 0.051 | 247 | 0.066351 | 228.6 | 0.096 | 254 | 0.111 | 236.7 | 0.175 | 263 | 0.191
[16 empty] | 223.2 | 0.05 | 248 | 0.066351 | 229.5 | 0.096 | 255 | 0.11 | 237.6 | 0.174 | 264 | 0.191
[16 empty] | 224.1 | 0.05 | 249 | 0.066351 | 230.4 | 0.095 | 256 | 0.11 | 238.5 | 0.173 | 265 | 0.19
[16 empty] | 225 | 0.05 | 250 | 0.066351 | 231.3 | 0.094 | 257 | 0.109 | 239.4 | 0.171 | 266 | 0.186
[16 empty] | 225.9 | 0.049 | 251 | 0.066351 | 232.2 | 0.093 | 258 | 0.109 | 240.3 | 0.17 | 267 | 0.185
[16 empty] | 226.8 | 0.049 | 252 | 0.066351 | 233.1 | 0.093 | 259 | 0.108 | 241.2 | 0.169 | 268 | 0.184
[16 empty] | 227.7 | 0.049 | 253 | 0.066351 | 234 | 0.092 | 260 | 0.108 | 242.1 | 0.168 | 269 | 0.183
[16 empty] | 228.6 | 0.048 | 254 | 0.065023 | 234.9 | 0.092 | 261 | 0.108 | 243 | 0.167 | 270 | 0.183
[16 empty] | 229.5 | 0.048 | 255 | 0.065023 | 235.8 | 0.091 | 262 | 0.108 | 243.9 | 0.165 | 271 | 0.183
[16 empty] | 230.4 | 0.048 | 256 | 0.065023 | 236.7 | 0.09 | 263 | 0.108 | 244.8 | 0.164 | 272 | 0.182
[16 empty] | 231.3 | 0.047 | 257 | 0.065023 | 237.6 | 0.09 | 264 | 0.107 | 245.7 | 0.163 | 273 | 0.177
[16 empty] | 232.2 | 0.047 | 258 | 0.065023 | 238.5 | 0.089 | 265 | 0.107 | 246.6 | 0.162 | 274 | 0.177
[16 empty] | 233.1 | 0.047 | 259 | 0.060901 | 239.4 | 0.088 | 266 | 0.102 | 247.5 | 0.161 | 275 | 0.176
[16 empty] | 234 | 0.047 | 260 | 0.060901 | 240.3 | 0.088 | 267 | 0.102 | 248.4 | 0.16 | 276 | 0.175
[16 empty] | 234.9 | 0.046 | 261 | 0.060901 | 241.2 | 0.087 | 268 | 0.102 | 249.3 | 0.159 | 277 | 0.175
[16 empty] | 235.8 | 0.046 | 262 | 0.060901 | 242.1 | 0.087 | 269 | 0.102 | 250.2 | 0.157 | 278 | 0.175
[16 empty] | 236.7 | 0.046 | 263 | 0.060901 | 243 | 0.086 | 270 | 0.101 | 250.2 | 0.007 | 279 | 0.173
[16 empty] | 237.6 | 0.045 | 264 | 0.060182 | 243.9 | 0.086 | 271 | 0.101 | 468 | 0.003 | 280 | 0.169
[16 empty] | 238.5 | 0.045 | 265 | 0.060182 | 244.8 | 0.085 | 272 | 0.101 | 6300 | 0.003 | 281 | 0.169
[16 empty] | 239.4 | 0.045 | 266 | 0.060182 | 245.7 | 0.084 | 273 | 0.1 |  |  | 282 | 0.168
[16 empty] | 240.3 | 0.045 | 267 | 0.060182 | 246.6 | 0.084 | 274 | 0.1 |  |  | 283 | 0.168
[16 empty] | 241.2 | 0.044 | 268 | 0.059455 | 247.5 | 0.083 | 275 | 0.1 |  |  | 284 | 0.166
[16 empty] | 242.1 | 0.044 | 269 | 0.059455 | 248.4 | 0.083 | 276 | 0.1 |  |  | 285 | 0.166
[16 empty] | 243 | 0.044 | 270 | 0.059455 | 249.3 | 0.082 | 277 | 0.1 |  |  | 286 | 0.166
[16 empty] | 243.9 | 0.044 | 271 | 0.059455 | 250.2 | 0.082 | 278 | 0.098 |  |  | 287 | 0.165
[16 empty] | 244.8 | 0.043 | 272 | 0.059455 | 250.2 | 0.007 | 279 | 0.098 |  |  | 288 | 0.164
[16 empty] | 245.7 | 0.043 | 273 | 0.059455 | 468 | 0.003 | 280 | 0.098 |  |  | 289 | 0.161
[16 empty] | 246.6 | 0.043 | 274 | 0.057982 | 6300 | 0.003 | 281 | 0.094 |  |  | 290 | 0.16
[16 empty] | 247.5 | 0.043 | 500 | 0.05 |  |  | 282 | 0.094 |  |  | 291 | 0.159
[16 empty] | 248.4 | 0.042 | 500 | 0.033 |  |  | 283 | 0.094 |  |  | 292 | 0.159
[16 empty] | 249.3 | 0.042 | 1000 | 0.033 |  |  | 284 | 0.093 |  |  | 293 | 0.158
[16 empty] | 250.2 | 0.042 | 6300 | 0.022 |  |  | 285 | 0.093 |  |  | 294 | 0.158
[16 empty] | 250.2 | 0.007 |  |  |  |  | 286 | 0.093 |  |  | 295 | 0.158
[16 empty] | 468 | 0.003 |  |  |  |  | 287 | 0.093 |  |  | 296 | 0.157
[16 empty] | 6300 | 0.003 |  |  |  |  | 288 | 0.093 |  |  | 297 | 0.152
[22 empty] | 289 | 0.091 |  |  | 298 | 0.152
[22 empty] | 290 | 0.091 |  |  | 300 | 0.151
[22 empty] | 291 | 0.091 |  |  | 300 | 0.061
[22 empty] | 292 | 0.091 |  |  | 500 | 0.05
[22 empty] | 293 | 0.091 |  |  | 500 | 0.033
[22 empty] | 294 | 0.091 |  |  | 1000 | 0.033
[22 empty] | 295 | 0.09 |  |  | 6300 | 0.022
[22 empty] | 296 | 0.09
[22 empty] | 297 | 0.09
[22 empty] | 298 | 0.086
[22 empty] | 300 | 0.086
[22 empty] | 300 | 0.06
[22 empty] | 500 | 0.05
[22 empty] | 500 | 0.033
[22 empty] | 1000 | 0.033
[22 empty] | 6300 | 0.022

## S&C "QR" Speed
S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter
S&C "QR" Speed | [11 empty] | S&C "QR" Speed | [11 empty] | S&C "QR" Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025
Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information.
2QR |  |  |  | 3QR |  |  |  | 5QR |  |  |  | 7QR |  |  |  | 8QR |  |  |  | 10QR |  |  |  | 15QR |  |  |  | 20QR
Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s
4 | 300.046 | 5 | 300.061 | 6 | 63.305 | 7 | 63.3191 | 8 | 20.072 | 9 | 20.0858 | 10.8 | 34.76 | 12 | 34.777 | 11.7 | 63.611 | 13 | 63.627 | 14.4 | 2000.885 | 16 | 2000.902 | 20.7 | 279.366 | 23 | 279.382 | 27.9 | 426.113 | 31 | 426.127
5 | 8.485 | 6 | 8.5 | 7 | 13.626 | 8 | 13.6413 | 9 | 8.99 | 10 | 9.0038 | 11.7 | 14.818 | 13 | 14.833 | 12.6 | 22.96 | 14 | 22.975 | 15.3 | 48.673 | 17 | 48.687 | 21.6 | 45.582 | 24 | 45.596 | 28.8 | 69.912 | 32 | 69.927
6 | 3.831 | 7 | 3.846 | 8 | 7.217 | 9 | 7.233 | 9.9 | 5.587 | 11 | 5.6018 | 12.6 | 9.153 | 14 | 9.168 | 13.5 | 13.619 | 15 | 13.633 | 16.2 | 23.64 | 18 | 23.654 | 22.5 | 24.35 | 25 | 24.366 | 29.7 | 37.542 | 33 | 37.558
7 | 2.542 | 8 | 2.558 | 9 | 4.733 | 10 | 4.7497 | 10.8 | 3.951 | 12 | 3.9663 | 13.5 | 6.49 | 15 | 6.504 | 14.4 | 9.493 | 16 | 9.508 | 17.1 | 15.316 | 19 | 15.333 | 23.4 | 16.402 | 26 | 16.418 | 30.6 | 25.416 | 34 | 25.433
8 | 1.914 | 9 | 1.929 | 9.9 | 3.43 | 11 | 3.4434 | 11.7 | 2.998 | 13 | 3.0122 | 14.4 | 4.952 | 16 | 4.966 | 15.3 | 7.18 | 17 | 7.193 | 18 | 11.173 | 20 | 11.187 | 24.3 | 12.249 | 27 | 12.262 | 31.5 | 19.074 | 35 | 19.087
9 | 1.52 | 10 | 1.535 | 10.8 | 2.637 | 12 | 2.6518 | 12.6 | 2.38 | 14 | 2.3934 | 15.3 | 3.955 | 17 | 3.968 | 16.2 | 5.706 | 18 | 5.721 | 18.9 | 8.7 | 21 | 8.716 | 25.2 | 9.701 | 28 | 9.716 | 32.4 | 15.178 | 36 | 15.193
9.9 | 1.243 | 11 | 1.258 | 11.7 | 2.108 | 13 | 2.1247 | 13.5 | 1.949 | 15 | 1.9622 | 16.2 | 3.26 | 18 | 3.275 | 17.1 | 4.69 | 19 | 4.704 | 19.8 | 7.062 | 22 | 7.077 | 26.1 | 7.982 | 29 | 7.996 | 33.3 | 12.544 | 37 | 12.56
10.8 | 1.044 | 12 | 1.058 | 12.6 | 1.733 | 14 | 1.7497 | 14.4 | 1.633 | 16 | 1.6497 | 17.1 | 2.75 | 19 | 2.766 | 18 | 3.949 | 20 | 3.962 | 20.7 | 5.9 | 23 | 5.916 | 27 | 6.745 | 30 | 6.76 | 34.2 | 10.647 | 38 | 10.66
11.7 | 0.889 | 13 | 0.902 | 13.5 | 1.456 | 15 | 1.4705 | 15.3 | 1.393 | 17 | 1.408 | 18 | 2.361 | 20 | 2.375 | 18.9 | 3.387 | 21 | 3.402 | 21.6 | 5.035 | 24 | 5.05 | 27.9 | 5.814 | 31 | 5.827 | 35.1 | 9.216 | 39 | 9.233
12.6 | 0.776 | 14 | 0.791 | 14.4 | 1.244 | 16 | 1.258 | 16.2 | 1.206 | 18 | 1.2205 | 18.9 | 2.056 | 21 | 2.068 | 19.8 | 2.947 | 22 | 2.96 | 22.5 | 4.368 | 25 | 4.383 | 28.8 | 5.089 | 32 | 5.102 | 36 | 8.1 | 40 | 8.116
13.5 | 0.686 | 15 | 0.702 | 15.3 | 1.077 | 17 | 1.0913 | 17.1 | 1.056 | 19 | 1.0705 | 19.8 | 1.81 | 22 | 1.825 | 20.7 | 2.595 | 23 | 2.61 | 23.4 | 3.839 | 26 | 3.852 | 29.7 | 4.509 | 33 | 4.525 | 36.9 | 7.205 | 41 | 7.218
14.4 | 0.606 | 16 | 0.621 | 16.2 | 0.943 | 18 | 0.958 | 18 | 0.934 | 20 | 0.94967 | 20.7 | 1.61 | 23 | 1.625 | 21.6 | 2.307 | 24 | 2.321 | 24.3 | 3.41 | 27 | 3.425 | 30.6 | 4.035 | 34 | 4.05 | 37.8 | 6.473 | 42 | 6.487
15.3 | 0.549 | 17 | 0.566 | 17.1 | 0.834 | 19 | 0.84967 | 18.9 | 0.833 | 21 | 0.84967 | 21.6 | 1.443 | 24 | 1.458 | 22.5 | 2.068 | 25 | 2.083 | 25.2 | 3.056 | 28 | 3.071 | 31.5 | 3.641 | 35 | 3.658 | 38.7 | 5.863 | 43 | 5.877
16.2 | 0.493 | 18 | 0.508 | 18 | 0.743 | 20 | 0.758 | 19.8 | 0.749 | 22 | 0.76217 | 22.5 | 1.302 | 25 | 1.316 | 23.4 | 1.867 | 26 | 1.883 | 26.1 | 2.759 | 29 | 2.775 | 32.4 | 3.309 | 36 | 3.325 | 39.6 | 5.347 | 44 | 5.362
17.1 | 0.454 | 19 | 0.468 | 18.9 | 0.667 | 21 | 0.683 | 20.7 | 0.677 | 23 | 0.69134 | 23.4 | 1.183 | 26 | 1.2 | 24.3 | 1.696 | 27 | 1.71 | 27 | 2.507 | 30 | 2.525 | 33.3 | 3.026 | 37 | 3.041 | 40.5 | 4.906 | 45 | 4.921
18 | 0.414 | 20 | 0.429 | 19.8 | 0.603 | 22 | 0.61634 | 21.6 | 0.616 | 24 | 0.62884 | 24.3 | 1.08 | 27 | 1.093 | 25.2 | 1.549 | 28 | 1.566 | 27.9 | 2.291 | 31 | 2.308 | 34.2 | 2.781 | 38 | 2.796 | 41.4 | 4.525 | 46 | 4.541
18.9 | 0.383 | 21 | 0.4 | 20.7 | 0.548 | 23 | 0.56217 | 22.5 | 0.562 | 25 | 0.57675 | 25.2 | 0.99 | 28 | 1.004 | 26.1 | 1.421 | 29 | 1.435 | 28.8 | 2.104 | 32 | 2.118 | 35.1 | 2.568 | 39 | 2.583 | 42.3 | 4.192 | 47 | 4.208
19.8 | 0.353 | 22 | 0.366 | 21.6 | 0.5 | 24 | 0.51634 | 23.4 | 0.516 | 26 | 0.533 | 26.1 | 0.912 | 29 | 0.927 | 27 | 1.31 | 30 | 1.325 | 29.7 | 1.941 | 33 | 1.958 | 36 | 2.381 | 40 | 2.396 | 43.2 | 3.899 | 48 | 3.916
20.7 | 0.328 | 23 | 0.341 | 22.5 | 0.459 | 25 | 0.47467 | 24.3 | 0.476 | 27 | 0.49134 | 27 | 0.843 | 30 | 0.858 | 27.9 | 1.212 | 31 | 1.227 | 30.6 | 1.797 | 34 | 1.81 | 36.9 | 2.216 | 41 | 2.233 | 44.1 | 3.639 | 49 | 3.654
21.6 | 0.306 | 24 | 0.321 | 23.4 | 0.422 | 26 | 0.43509 | 25.2 | 0.44 | 28 | 0.45384 | 27.9 | 0.783 | 31 | 0.8 | 28.8 | 1.125 | 32 | 1.141 | 31.5 | 1.67 | 35 | 1.685 | 37.8 | 2.069 | 42 | 2.083 | 45 | 3.407 | 50 | 3.425
22.5 | 0.285 | 25 | 0.3 | 24.3 | 0.39 | 27 | 0.40384 | 26.1 | 0.408 | 29 | 0.42467 | 28.8 | 0.728 | 32 | 0.743 | 29.7 | 1.047 | 33 | 1.06 | 32.4 | 1.557 | 36 | 1.571 | 38.7 | 1.937 | 43 | 1.952 | 45.9 | 3.2 | 51 | 3.216
23.4 | 0.268 | 26 | 0.283 | 25.2 | 0.362 | 28 | 0.37675 | 27 | 0.38 | 30 | 0.39342 | 29.7 | 0.68 | 33 | 0.693 | 30.6 | 0.978 | 34 | 0.991 | 33.3 | 1.455 | 37 | 1.468 | 39.6 | 1.819 | 44 | 1.833 | 46.8 | 3.013 | 52 | 3.027
24.3 | 0.252 | 27 | 0.266 | 26.1 | 0.337 | 29 | 0.35175 | 27.9 | 0.355 | 31 | 0.36842 | 30.6 | 0.636 | 34 | 0.65 | 31.5 | 0.915 | 35 | 0.929 | 34.2 | 1.364 | 38 | 1.377 | 40.5 | 1.712 | 45 | 1.727 | 47.7 | 2.843 | 53 | 2.858
25.2 | 0.236 | 28 | 0.25 | 27 | 0.314 | 30 | 0.32884 | 28.8 | 0.332 | 32 | 0.3455 | 31.5 | 0.597 | 35 | 0.61 | 32.4 | 0.859 | 36 | 0.875 | 35.1 | 1.282 | 39 | 1.296 | 41.4 | 1.615 | 46 | 1.629 | 48.6 | 2.689 | 54 | 2.704
26.1 | 0.224 | 29 | 0.241 | 27.9 | 0.294 | 31 | 0.308 | 29.7 | 0.312 | 33 | 0.32675 | 32.4 | 0.561 | 36 | 0.575 | 33.3 | 0.808 | 37 | 0.825 | 36 | 1.207 | 40 | 1.221 | 42.3 | 1.527 | 47 | 1.541 | 49.5 | 2.549 | 55 | 2.562
27 | 0.212 | 30 | 0.227 | 28.8 | 0.276 | 32 | 0.29134 | 30.6 | 0.293 | 34 | 0.308 | 33.3 | 0.529 | 37 | 0.543 | 34.2 | 0.762 | 38 | 0.777 | 36.9 | 1.139 | 41 | 1.152 | 43.2 | 1.446 | 48 | 1.46 | 50.4 | 2.42 | 56 | 2.435
27.9 | 0.201 | 31 | 0.216 | 29.7 | 0.259 | 33 | 0.27467 | 31.5 | 0.276 | 35 | 0.29134 | 34.2 | 0.499 | 38 | 0.516 | 35.1 | 0.719 | 39 | 0.733 | 37.8 | 1.077 | 42 | 1.091 | 44.1 | 1.372 | 49 | 1.385 | 51.3 | 2.302 | 57 | 2.316
28.8 | 0.192 | 32 | 0.208 | 30.6 | 0.244 | 34 | 0.258 | 32.4 | 0.261 | 36 | 0.27467 | 35.1 | 0.472 | 39 | 0.485 | 36 | 0.681 | 40 | 0.693 | 38.7 | 1.02 | 43 | 1.033 | 45 | 1.304 | 50 | 1.318 | 52.2 | 2.192 | 58 | 2.208
29.7 | 0.183 | 33 | 0.2 | 31.5 | 0.23 | 35 | 0.24342 | 33.3 | 0.247 | 37 | 0.26009 | 36 | 0.448 | 40 | 0.462 | 36.9 | 0.645 | 41 | 0.66 | 39.6 | 0.967 | 44 | 0.983 | 45.9 | 1.241 | 51 | 1.258 | 53.1 | 2.092 | 59 | 2.108
30.6 | 0.174 | 34 | 0.191 | 32.4 | 0.218 | 36 | 0.233 | 34.2 | 0.234 | 38 | 0.24967 | 36.9 | 0.425 | 41 | 0.441 | 37.8 | 0.612 | 42 | 0.627 | 40.5 | 0.919 | 45 | 0.933 | 46.8 | 1.183 | 52 | 1.2 | 54 | 1.998 | 60 | 2.012
31.5 | 0.167 | 35 | 0.183 | 33.3 | 0.206 | 37 | 0.2205 | 35.1 | 0.222 | 39 | 0.23509 | 37.8 | 0.404 | 42 | 0.418 | 38.7 | 0.582 | 43 | 0.596 | 41.4 | 0.875 | 46 | 0.891 | 47.7 | 1.129 | 53 | 1.143 | 54.9 | 1.912 | 61 | 1.927
32.4 | 0.16 | 36 | 0.176 | 34.2 | 0.196 | 38 | 0.21009 | 36 | 0.211 | 40 | 0.22467 | 38.7 | 0.384 | 43 | 0.4 | 39.6 | 0.554 | 44 | 0.568 | 42.3 | 0.834 | 47 | 0.85 | 48.6 | 1.079 | 54 | 1.093 | 55.8 | 1.831 | 62 | 1.843
33.3 | 0.154 | 37 | 0.168 | 35.1 | 0.186 | 39 | 0.20106 | 36.9 | 0.201 | 41 | 0.21634 | 39.6 | 0.366 | 44 | 0.383 | 40.5 | 0.528 | 45 | 0.543 | 43.2 | 0.795 | 48 | 0.81 | 49.5 | 1.033 | 55 | 1.05 | 56.7 | 1.755 | 63 | 1.768
34.2 | 0.147 | 38 | 0.164 | 36 | 0.177 | 40 | 0.19273 | 37.8 | 0.192 | 42 | 0.208 | 40.5 | 0.35 | 45 | 0.366 | 41.4 | 0.504 | 46 | 0.518 | 44.1 | 0.76 | 49 | 0.775 | 50.4 | 0.989 | 56 | 1.002 | 57.6 | 1.685 | 64 | 1.7
35.1 | 0.142 | 39 | 0.158 | 36.9 | 0.168 | 41 | 0.18439 | 38.7 | 0.183 | 43 | 0.19967 | 41.4 | 0.334 | 46 | 0.35 | 42.3 | 0.482 | 47 | 0.496 | 45 | 0.727 | 50 | 0.741 | 51.3 | 0.949 | 57 | 0.962 | 58.5 | 1.619 | 65 | 1.633
36 | 0.137 | 40 | 0.152 | 37.8 | 0.161 | 42 | 0.17606 | 39.6 | 0.175 | 44 | 0.19134 | 42.3 | 0.32 | 47 | 0.333 | 43.2 | 0.461 | 48 | 0.475 | 45.9 | 0.696 | 51 | 0.71 | 52.2 | 0.911 | 58 | 0.925 | 59.4 | 1.557 | 66 | 1.571
36.9 | 0.132 | 41 | 0.148 | 38.7 | 0.154 | 43 | 0.16842 | 40.5 | 0.167 | 45 | 0.183 | 43.2 | 0.306 | 48 | 0.321 | 44.1 | 0.441 | 49 | 0.458 | 46.8 | 0.667 | 52 | 0.683 | 53.1 | 0.875 | 59 | 0.891 | 60.3 | 1.499 | 67 | 1.512
37.8 | 0.127 | 42 | 0.143 | 39.6 | 0.147 | 44 | 0.16078 | 41.4 | 0.16 | 46 | 0.17606 | 44.1 | 0.293 | 49 | 0.308 | 45 | 0.423 | 50 | 0.437 | 47.7 | 0.64 | 53 | 0.654 | 54 | 0.842 | 60 | 0.858 | 61.2 | 1.444 | 68 | 1.458
38.7 | 0.123 | 43 | 0.14 | 40.5 | 0.141 | 45 | 0.158 | 42.3 | 0.154 | 47 | 0.16842 | 45 | 0.282 | 50 | 0.296 | 45.9 | 0.406 | 51 | 0.421 | 48.6 | 0.614 | 54 | 0.629 | 54.9 | 0.81 | 61 | 0.825 | 62.1 | 1.393 | 69 | 1.408
39.6 | 0.119 | 44 | 0.134 | 41.4 | 0.135 | 46 | 0.15106 | 43.2 | 0.147 | 48 | 0.16495 | 45.9 | 0.27 | 51 | 0.285 | 46.8 | 0.39 | 52 | 0.404 | 49.5 | 0.591 | 55 | 0.608 | 55.8 | 0.78 | 62 | 0.793 | 63 | 1.344 | 70 | 1.358
40.5 | 0.115 | 45 | 0.133 | 42.3 | 0.13 | 47 | 0.14412 | 44.1 | 0.142 | 49 | 0.158 | 46.8 | 0.26 | 52 | 0.275 | 47.7 | 0.375 | 53 | 0.391 | 50.4 | 0.568 | 56 | 0.583 | 56.7 | 0.753 | 63 | 0.766 | 63.9 | 1.298 | 71 | 1.312
41.4 | 0.112 | 46 | 0.127 | 43.2 | 0.125 | 48 | 0.14134 | 45 | 0.136 | 50 | 0.15175 | 47.7 | 0.25 | 53 | 0.266 | 48.6 | 0.361 | 54 | 0.375 | 51.3 | 0.547 | 57 | 0.56 | 57.6 | 0.726 | 64 | 0.741 | 64.8 | 1.255 | 72 | 1.268
42.3 | 0.108 | 47 | 0.125 | 44.1 | 0.12 | 49 | 0.13508 | 45.9 | 0.131 | 51 | 0.14828 | 48.6 | 0.241 | 54 | 0.258 | 49.5 | 0.348 | 55 | 0.362 | 52.2 | 0.527 | 58 | 0.541 | 58.5 | 0.701 | 65 | 0.716 | 65.7 | 1.213 | 73 | 1.227
43.2 | 0.105 | 48 | 0.119 | 45 | 0.115 | 50 | 0.133 | 46.8 | 0.126 | 52 | 0.14273 | 49.5 | 0.232 | 55 | 0.25 | 50.4 | 0.335 | 56 | 0.35 | 53.1 | 0.508 | 59 | 0.525 | 59.4 | 0.678 | 66 | 0.691 | 66.6 | 1.174 | 74 | 1.191
44.1 | 0.102 | 49 | 0.118 | 45.9 | 0.111 | 51 | 0.12606 | 47.7 | 0.122 | 53 | 0.13578 | 50.4 | 0.224 | 56 | 0.241 | 51.3 | 0.323 | 57 | 0.337 | 54 | 0.491 | 60 | 0.508 | 60.3 | 0.655 | 67 | 0.668 | 67.5 | 1.137 | 75 | 1.152
45 | 0.099 | 50 | 0.116 | 46.8 | 0.107 | 52 | 0.12467 | 48.6 | 0.118 | 54 | 0.133 | 51.3 | 0.216 | 57 | 0.233 | 52.2 | 0.312 | 58 | 0.327 | 54.9 | 0.474 | 61 | 0.491 | 61.2 | 0.634 | 68 | 0.65 | 68.4 | 1.102 | 76 | 1.116
45.9 | 0.096 | 51 | 0.111 | 47.7 | 0.103 | 53 | 0.11841 | 49.5 | 0.114 | 55 | 0.13092 | 52.2 | 0.209 | 58 | 0.225 | 53.1 | 0.301 | 59 | 0.316 | 55.8 | 0.458 | 62 | 0.475 | 62.1 | 0.614 | 69 | 0.627 | 69.3 | 1.068 | 77 | 1.083
46.8 | 0.094 | 52 | 0.109 | 48.6 | 0.1 | 54 | 0.11634 | 50.4 | 0.11 | 56 | 0.12606 | 53.1 | 0.202 | 59 | 0.216 | 54 | 0.291 | 60 | 0.308 | 56.7 | 0.443 | 63 | 0.458 | 63 | 0.595 | 70 | 0.608 | 70.2 | 1.036 | 78 | 1.052
47.7 | 0.091 | 53 | 0.108 | 49.5 | 0.097 | 55 | 0.11079 | 51.3 | 0.106 | 57 | 0.12328 | 54 | 0.195 | 60 | 0.21 | 54.9 | 0.282 | 61 | 0.296 | 57.6 | 0.429 | 64 | 0.443 | 63.9 | 0.576 | 71 | 0.591 | 71.1 | 1.006 | 79 | 1.021
48.6 | 0.088 | 54 | 0.102 | 50.4 | 0.093 | 56 | 0.1094 | 52.2 | 0.103 | 58 | 0.11841 | 54.9 | 0.189 | 61 | 0.206 | 55.8 | 0.272 | 62 | 0.287 | 58.5 | 0.415 | 65 | 0.429 | 64.8 | 0.559 | 72 | 0.575 | 72 | 0.977 | 80 | 0.991
49.5 | 0.086 | 55 | 0.101 | 51.3 | 0.09 | 57 | 0.108 | 53.1 | 0.1 | 59 | 0.11634 | 55.8 | 0.183 | 62 | 0.2 | 56.7 | 0.264 | 63 | 0.277 | 59.4 | 0.402 | 66 | 0.416 | 65.7 | 0.542 | 73 | 0.558 | 72.9 | 0.949 | 81 | 0.966
50.4 | 0.084 | 56 | 0.1 | 52.2 | 0.088 | 58 | 0.10243 | 54 | 0.097 | 60 | 0.11079 | 56.7 | 0.177 | 63 | 0.193 | 57.6 | 0.256 | 64 | 0.268 | 60.3 | 0.39 | 67 | 0.404 | 66.6 | 0.527 | 74 | 0.541 | 73.8 | 0.923 | 82 | 0.937
51.3 | 0.082 | 57 | 0.1 | 53.1 | 0.085 | 59 | 0.10105 | 54.9 | 0.094 | 61 | 0.1094 | 57.6 | 0.172 | 64 | 0.186 | 58.5 | 0.248 | 65 | 0.262 | 61.2 | 0.378 | 68 | 0.391 | 67.5 | 0.512 | 75 | 0.527 | 74.7 | 0.897 | 83 | 0.91
52.2 | 0.081 | 58 | 0.098 | 54 | 0.082 | 60 | 0.099673 | 55.8 | 0.091 | 62 | 0.108 | 58.5 | 0.167 | 65 | 0.183 | 59.4 | 0.24 | 66 | 0.254 | 62.1 | 0.367 | 69 | 0.383 | 68.4 | 0.497 | 76 | 0.51 | 75.6 | 0.873 | 84 | 0.887
53.1 | 0.079 | 59 | 0.093 | 54.9 | 0.08 | 61 | 0.09414 | 56.7 | 0.088 | 63 | 0.10243 | 59.4 | 0.162 | 66 | 0.177 | 60.3 | 0.233 | 67 | 0.25 | 63 | 0.356 | 70 | 0.371 | 69.3 | 0.483 | 77 | 0.5 | 76.5 | 0.85 | 85 | 0.866
54 | 0.077 | 60 | 0.093 | 55.8 | 0.078 | 62 | 0.092739 | 57.6 | 0.086 | 64 | 0.10105 | 60.3 | 0.157 | 67 | 0.175 | 61.2 | 0.227 | 68 | 0.241 | 63.9 | 0.346 | 71 | 0.36 | 70.2 | 0.47 | 78 | 0.485 | 77.4 | 0.827 | 86 | 0.841
54.9 | 0.075 | 61 | 0.091 | 56.7 | 0.076 | 63 | 0.091332 | 58.5 | 0.084 | 65 | 0.099673 | 61.2 | 0.153 | 68 | 0.168 | 62.1 | 0.22 | 69 | 0.235 | 64.8 | 0.336 | 72 | 0.35 | 71.1 | 0.457 | 79 | 0.475 | 78.3 | 0.806 | 87 | 0.821
55.8 | 0.073 | 62 | 0.09 | 57.6 | 0.073 | 64 | 0.089925 | 59.4 | 0.081 | 66 | 0.098297 | 62.1 | 0.149 | 69 | 0.165 | 63 | 0.214 | 70 | 0.227 | 65.7 | 0.327 | 73 | 0.341 | 72 | 0.445 | 80 | 0.46 | 79.2 | 0.786 | 88 | 0.8
56.7 | 0.072 | 63 | 0.086 | 58.5 | 0.071 | 65 | 0.085744 | 60.3 | 0.079 | 67 | 0.09414 | 63 | 0.144 | 70 | 0.159 | 63.9 | 0.208 | 71 | 0.225 | 66.6 | 0.318 | 74 | 0.333 | 72.9 | 0.434 | 81 | 0.45 | 80.1 | 0.766 | 89 | 0.783
57.6 | 0.07 | 64 | 0.085 | 59.4 | 0.07 | 66 | 0.085057 | 61.2 | 0.077 | 68 | 0.092739 | 63.9 | 0.141 | 71 | 0.158 | 64.8 | 0.202 | 72 | 0.216 | 67.5 | 0.309 | 75 | 0.325 | 73.8 | 0.423 | 82 | 0.437 | 81 | 0.747 | 90 | 0.76
58.5 | 0.069 | 65 | 0.084 | 60.3 | 0.068 | 67 | 0.08301 | 62.1 | 0.075 | 69 | 0.091332 | 64.8 | 0.137 | 72 | 0.152 | 65.7 | 0.197 | 73 | 0.21 | 68.4 | 0.301 | 76 | 0.316 | 74.7 | 0.412 | 83 | 0.427 | 81.9 | 0.729 | 91 | 0.743
59.4 | 0.067 | 66 | 0.083 | 61.2 | 0.066 | 68 | 0.08301 | 63 | 0.073 | 70 | 0.089925 | 65.7 | 0.133 | 73 | 0.15 | 66.6 | 0.192 | 74 | 0.208 | 69.3 | 0.293 | 77 | 0.308 | 75.6 | 0.402 | 84 | 0.416 | 82.8 | 0.711 | 92 | 0.725
60.3 | 0.066 | 67 | 0.083 | 62.1 | 0.064 | 69 | 0.081649 | 63.9 | 0.071 | 71 | 0.085744 | 66.6 | 0.13 | 74 | 0.144 | 67.5 | 0.187 | 75 | 0.202 | 70.2 | 0.286 | 78 | 0.3 | 76.5 | 0.392 | 85 | 0.408 | 83.7 | 0.694 | 93 | 0.708
61.2 | 0.064 | 68 | 0.082 | 63 | 0.063 | 70 | 0.077503 | 64.8 | 0.07 | 72 | 0.085057 | 67.5 | 0.127 | 75 | 0.143 | 68.4 | 0.182 | 76 | 0.198 | 71.1 | 0.278 | 79 | 0.293 | 77.4 | 0.382 | 86 | 0.396 | 84.6 | 0.678 | 94 | 0.693
62.1 | 0.063 | 69 | 0.078 | 63.9 | 0.061 | 71 | 0.076797 | 65.7 | 0.068 | 73 | 0.08301 | 68.4 | 0.123 | 76 | 0.14 | 69.3 | 0.177 | 77 | 0.193 | 72 | 0.271 | 80 | 0.285 | 78.3 | 0.373 | 87 | 0.387 | 85.5 | 0.663 | 95 | 0.677
63 | 0.062 | 70 | 0.077 | 64.8 | 0.06 | 72 | 0.076088 | 66.6 | 0.066 | 74 | 0.08301 | 69.3 | 0.12 | 77 | 0.135 | 70.2 | 0.173 | 78 | 0.19 | 72.9 | 0.265 | 81 | 0.279 | 79.2 | 0.364 | 88 | 0.379 | 86.4 | 0.647 | 96 | 0.66
63.9 | 0.061 | 71 | 0.076 | 65.7 | 0.058 | 73 | 0.074661 | 67.5 | 0.065 | 75 | 0.081649 | 70.2 | 0.118 | 78 | 0.133 | 71.1 | 0.169 | 79 | 0.184 | 73.8 | 0.258 | 82 | 0.275 | 80.1 | 0.356 | 89 | 0.368 | 87.3 | 0.633 | 97 | 0.65
64.8 | 0.06 | 72 | 0.075 | 66.6 | 0.057 | 74 | 0.07466 | 68.4 | 0.063 | 76 | 0.077503 | 71.1 | 0.115 | 79 | 0.132 | 72 | 0.165 | 80 | 0.182 | 74.7 | 0.252 | 83 | 0.266 | 81 | 0.348 | 90 | 0.362 | 88.2 | 0.619 | 98 | 0.633
65.7 | 0.058 | 73 | 0.075 | 67.5 | 0.056 | 75 | 0.073231 | 69.3 | 0.062 | 77 | 0.076797 | 72 | 0.112 | 80 | 0.127 | 72.9 | 0.161 | 81 | 0.176 | 75.6 | 0.246 | 84 | 0.26 | 81.9 | 0.34 | 91 | 0.354 | 89.1 | 0.605 | 99 | 0.618
66.6 | 0.057 | 74 | 0.075 | 68.4 | 0.055 | 76 | 0.069033 | 70.2 | 0.061 | 78 | 0.076088 | 72.9 | 0.11 | 81 | 0.125 | 73.8 | 0.157 | 82 | 0.173 | 76.5 | 0.24 | 85 | 0.254 | 82.8 | 0.332 | 92 | 0.346 | 90 | 0.592 | 100 | 0.608
67.5 | 0.056 | 75 | 0.073 | 69.3 | 0.053 | 77 | 0.068355 | 71.1 | 0.059 | 79 | 0.07466 | 73.8 | 0.107 | 82 | 0.125 | 74.7 | 0.153 | 83 | 0.168 | 77.4 | 0.235 | 86 | 0.25 | 83.7 | 0.325 | 93 | 0.341 | 90.9 | 0.58 | 101 | 0.593
68.4 | 0.055 | 76 | 0.069 | 70.2 | 0.052 | 78 | 0.067683 | 72 | 0.058 | 80 | 0.074661 | 74.7 | 0.105 | 83 | 0.119 | 75.6 | 0.15 | 84 | 0.166 | 78.3 | 0.229 | 87 | 0.243 | 84.6 | 0.318 | 94 | 0.333 | 91.8 | 0.567 | 102 | 0.583
69.3 | 0.054 | 77 | 0.069 | 71.1 | 0.051 | 79 | 0.066351 | 72.9 | 0.057 | 81 | 0.073231 | 75.6 | 0.102 | 84 | 0.118 | 76.5 | 0.146 | 85 | 0.161 | 79.2 | 0.224 | 88 | 0.241 | 85.5 | 0.311 | 95 | 0.325 | 92.7 | 0.555 | 103 | 0.568
70.2 | 0.053 | 78 | 0.068 | 72 | 0.05 | 80 | 0.066351 | 73.8 | 0.056 | 82 | 0.07323 | 76.5 | 0.1 | 85 | 0.116 | 77.4 | 0.143 | 86 | 0.159 | 80.1 | 0.219 | 89 | 0.233 | 86.4 | 0.304 | 96 | 0.318 | 93.6 | 0.544 | 104 | 0.558
71.1 | 0.053 | 79 | 0.068 | 72.9 | 0.049 | 81 | 0.066351 | 74.7 | 0.054 | 83 | 0.069033 | 77.4 | 0.098 | 86 | 0.115 | 78.3 | 0.14 | 87 | 0.157 | 81 | 0.215 | 90 | 0.229 | 87.3 | 0.298 | 97 | 0.312 | 94.5 | 0.533 | 105 | 0.55
72 | 0.052 | 80 | 0.068 | 73.8 | 0.048 | 82 | 0.065023 | 75.6 | 0.053 | 84 | 0.068355 | 78.3 | 0.096 | 87 | 0.111 | 79.2 | 0.137 | 88 | 0.152 | 81.9 | 0.21 | 91 | 0.225 | 88.2 | 0.292 | 98 | 0.308 | 95.4 | 0.522 | 106 | 0.535
72.9 | 0.051 | 81 | 0.066 | 74.7 | 0.047 | 83 | 0.065023 | 76.5 | 0.052 | 85 | 0.067683 | 79.2 | 0.094 | 88 | 0.109 | 80.1 | 0.134 | 89 | 0.15 | 82.8 | 0.206 | 92 | 0.218 | 89.1 | 0.286 | 99 | 0.3 | 96.3 | 0.512 | 107 | 0.527
73.8 | 0.05 | 82 | 0.066 | 75.6 | 0.046 | 84 | 0.060901 | 77.4 | 0.051 | 86 | 0.066351 | 80.1 | 0.092 | 89 | 0.108 | 81 | 0.131 | 90 | 0.148 | 83.7 | 0.201 | 93 | 0.216 | 90 | 0.28 | 100 | 0.293 | 97.2 | 0.502 | 108 | 0.516
74.7 | 0.049 | 83 | 0.066 | 76.5 | 0.045 | 85 | 0.060182 | 78.3 | 0.05 | 87 | 0.066351 | 81 | 0.09 | 90 | 0.107 | 81.9 | 0.129 | 91 | 0.143 | 84.6 | 0.197 | 94 | 0.21 | 90.9 | 0.274 | 101 | 0.291 | 98.1 | 0.492 | 109 | 0.508
75.6 | 0.049 | 84 | 0.066 | 77.4 | 0.045 | 86 | 0.060182 | 79.2 | 0.049 | 88 | 0.066351 | 81.9 | 0.088 | 91 | 0.102 | 82.8 | 0.126 | 92 | 0.141 | 85.5 | 0.193 | 95 | 0.208 | 91.8 | 0.269 | 102 | 0.283 | 99 | 0.482 | 110 | 0.5
76.5 | 0.048 | 85 | 0.065 | 78.3 | 0.044 | 87 | 0.059455 | 80.1 | 0.049 | 89 | 0.065023 | 82.8 | 0.087 | 92 | 0.102 | 83.7 | 0.123 | 93 | 0.14 | 86.4 | 0.189 | 96 | 0.202 | 92.7 | 0.263 | 103 | 0.277 | 99.9 | 0.473 | 111 | 0.487
77.4 | 0.047 | 86 | 0.065 | 79.2 | 0.043 | 88 | 0.059455 | 81 | 0.048 | 90 | 0.065023 | 83.7 | 0.085 | 93 | 0.101 | 84.6 | 0.121 | 94 | 0.136 | 87.3 | 0.185 | 97 | 0.201 | 93.6 | 0.258 | 104 | 0.275 | 100.8 | 0.464 | 112 | 0.479
78.3 | 0.046 | 87 | 0.061 | 80.1 | 0.042 | 500 | 0.048 | 81.9 | 0.047 | 91 | 0.060901 | 84.6 | 0.083 | 94 | 0.1 | 85.5 | 0.119 | 95 | 0.134 | 88.2 | 0.181 | 98 | 0.198 | 94.5 | 0.253 | 105 | 0.268 | 101.7 | 0.456 | 113 | 0.468
79.2 | 0.046 | 88 | 0.061 | 250.2 | 0.035 | 500 | 0.033 | 82.8 | 0.046 | 92 | 0.060901 | 85.5 | 0.082 | 95 | 0.098 | 86.4 | 0.116 | 96 | 0.133 | 89.1 | 0.178 | 99 | 0.193 | 95.4 | 0.249 | 106 | 0.262 | 102.6 | 0.447 | 114 | 0.46
80.1 | 0.045 | 89 | 0.06 | 250.2 | 0.007 | 1000 | 0.033 | 83.7 | 0.045 | 93 | 0.060183 | 86.4 | 0.08 | 96 | 0.094 | 87.3 | 0.114 | 97 | 0.132 | 90 | 0.174 | 100 | 0.191 | 96.3 | 0.244 | 107 | 0.258 | 103.5 | 0.439 | 115 | 0.452
81 | 0.044 | 90 | 0.059 | 468 | 0.003 | 6300 | 0.022 | 84.6 | 0.044 | 94 | 0.060182 | 87.3 | 0.079 | 97 | 0.093 | 88.2 | 0.112 | 98 | 0.127 | 90.9 | 0.171 | 101 | 0.186 | 97.2 | 0.239 | 108 | 0.254 | 104.4 | 0.431 | 116 | 0.446
81.9 | 0.044 | 91 | 0.059 | 6300 | 0.003 |  |  | 85.5 | 0.044 | 95 | 0.059455 | 88.2 | 0.077 | 98 | 0.093 | 89.1 | 0.11 | 99 | 0.126 | 91.8 | 0.168 | 102 | 0.183 | 98.1 | 0.235 | 109 | 0.25 | 105.3 | 0.423 | 117 | 0.437
82.8 | 0.043 | 92 | 0.059 |  |  |  |  | 86.4 | 0.043 | 96 | 0.059455 | 89.1 | 0.076 | 99 | 0.091 | 90 | 0.108 | 100 | 0.125 | 92.7 | 0.165 | 103 | 0.182 | 99 | 0.231 | 110 | 0.246 | 106.2 | 0.416 | 118 | 0.433
83.7 | 0.043 | 500 | 0.048 |  |  |  |  | 87.3 | 0.042 | 97 | 0.057982 | 90 | 0.075 | 100 | 0.091 | 90.9 | 0.106 | 101 | 0.123 | 93.6 | 0.162 | 104 | 0.177 | 99.9 | 0.227 | 111 | 0.241 | 107.1 | 0.409 | 119 | 0.425
84.6 | 0.042 | 500 | 0.033 |  |  |  |  | 250.2 | 0.035 | 500 | 0.048 | 90.9 | 0.073 | 101 | 0.09 | 91.8 | 0.104 | 102 | 0.118 | 94.5 | 0.159 | 105 | 0.175 | 100.8 | 0.223 | 112 | 0.237 | 108 | 0.402 | 120 | 0.416
85.5 | 0.042 | 1000 | 0.033 |  |  |  |  | 250.2 | 0.007 | 500 | 0.033 | 91.8 | 0.072 | 102 | 0.086 | 92.7 | 0.102 | 103 | 0.118 | 95.4 | 0.156 | 106 | 0.173 | 101.7 | 0.219 | 113 | 0.233 | 108.9 | 0.395 | 121 | 0.408
250.2 | 0.035 | 6300 | 0.022 |  |  |  |  | 468 | 0.003 | 1000 | 0.033 | 92.7 | 0.071 | 103 | 0.085 | 93.6 | 0.1 | 104 | 0.116 | 96.3 | 0.153 | 107 | 0.168 | 102.6 | 0.215 | 114 | 0.229 | 109.8 | 0.388 | 122 | 0.402
250.2 | 0.007 | [6 empty] | 6300 | 0.003 | 6300 | 0.022 | 93.6 | 0.07 | 104 | 0.085 | 94.5 | 0.098 | 105 | 0.115 | 97.2 | 0.15 | 108 | 0.166 | 103.5 | 0.211 | 115 | 0.225 | 110.7 | 0.381 | 123 | 0.396
468 | 0.003 | [10 empty] | 94.5 | 0.068 | 105 | 0.084 | 95.4 | 0.097 | 106 | 0.111 | 98.1 | 0.148 | 109 | 0.165 | 104.4 | 0.208 | 116 | 0.225 | 111.6 | 0.375 | 124 | 0.391
6300 | 0.003 | [10 empty] | 95.4 | 0.067 | 106 | 0.083 | 96.3 | 0.095 | 107 | 0.11 | 99 | 0.145 | 110 | 0.16 | 105.3 | 0.204 | 117 | 0.218 | 112.5 | 0.369 | 125 | 0.383
[12 empty] | 96.3 | 0.066 | 107 | 0.083 | 97.2 | 0.093 | 108 | 0.109 | 99.9 | 0.143 | 111 | 0.158 | 106.2 | 0.201 | 118 | 0.216 | 113.4 | 0.363 | 126 | 0.377
[12 empty] | 97.2 | 0.065 | 108 | 0.082 | 98.1 | 0.092 | 109 | 0.108 | 100.8 | 0.14 | 112 | 0.157 | 107.1 | 0.197 | 119 | 0.21 | 114.3 | 0.357 | 127 | 0.371
[12 empty] | 98.1 | 0.064 | 109 | 0.082 | 99 | 0.09 | 110 | 0.108 | 101.7 | 0.138 | 113 | 0.152 | 108 | 0.194 | 120 | 0.208 | 115.2 | 0.351 | 128 | 0.366
[12 empty] | 99 | 0.063 | 110 | 0.078 | 99.9 | 0.089 | 111 | 0.106 | 102.6 | 0.135 | 114 | 0.151 | 108.9 | 0.191 | 121 | 0.208 | 116.1 | 0.346 | 129 | 0.36
[12 empty] | 99.9 | 0.062 | 111 | 0.077 | 100.8 | 0.087 | 112 | 0.102 | 103.5 | 0.133 | 115 | 0.15 | 109.8 | 0.188 | 122 | 0.202 | 117 | 0.34 | 130 | 0.354
[12 empty] | 100.8 | 0.061 | 112 | 0.077 | 101.7 | 0.086 | 113 | 0.101 | 104.4 | 0.131 | 116 | 0.148 | 110.7 | 0.185 | 123 | 0.2 | 117.9 | 0.335 | 131 | 0.35
[12 empty] | 101.7 | 0.06 | 113 | 0.076 | 102.6 | 0.085 | 114 | 0.1 | 105.3 | 0.129 | 117 | 0.143 | 111.6 | 0.182 | 124 | 0.198 | 118.8 | 0.33 | 132 | 0.343
[12 empty] | 102.6 | 0.059 | 114 | 0.075 | 103.5 | 0.083 | 115 | 0.1 | 106.2 | 0.127 | 118 | 0.143 | 112.5 | 0.179 | 125 | 0.193 | 119.7 | 0.325 | 133 | 0.341
[12 empty] | 103.5 | 0.058 | 115 | 0.075 | 104.4 | 0.082 | 116 | 0.1 | 107.1 | 0.125 | 119 | 0.141 | 113.4 | 0.176 | 126 | 0.191 | 120.6 | 0.32 | 134 | 0.333
[12 empty] | 104.4 | 0.058 | 116 | 0.075 | 105.3 | 0.081 | 117 | 0.098 | 108 | 0.123 | 120 | 0.14 | 114.3 | 0.173 | 127 | 0.19 | 121.5 | 0.315 | 135 | 0.329
[12 empty] | 105.3 | 0.057 | 117 | 0.073 | 106.2 | 0.08 | 118 | 0.094 | 108.9 | 0.121 | 121 | 0.136 | 115.2 | 0.171 | 128 | 0.185 | 122.4 | 0.31 | 136 | 0.325
[12 empty] | 106.2 | 0.056 | 118 | 0.073 | 107.1 | 0.078 | 119 | 0.093 | 109.8 | 0.119 | 122 | 0.134 | 116.1 | 0.168 | 129 | 0.184 | 123.3 | 0.305 | 137 | 0.318
[12 empty] | 107.1 | 0.055 | 119 | 0.069 | 108 | 0.077 | 120 | 0.093 | 110.7 | 0.117 | 123 | 0.133 | 117 | 0.166 | 130 | 0.183 | 124.2 | 0.301 | 138 | 0.316
[12 empty] | 108 | 0.054 | 120 | 0.069 | 108.9 | 0.076 | 121 | 0.091 | 111.6 | 0.116 | 124 | 0.133 | 117.9 | 0.163 | 131 | 0.177 | 125.1 | 0.296 | 139 | 0.31
[12 empty] | 108.9 | 0.054 | 121 | 0.068 | 109.8 | 0.075 | 122 | 0.091 | 112.5 | 0.114 | 125 | 0.131 | 118.8 | 0.161 | 132 | 0.176 | 126 | 0.292 | 140 | 0.308
[12 empty] | 109.8 | 0.053 | 122 | 0.068 | 110.7 | 0.074 | 123 | 0.091 | 113.4 | 0.112 | 126 | 0.127 | 119.7 | 0.158 | 133 | 0.175 | 126.9 | 0.288 | 141 | 0.302
[12 empty] | 110.7 | 0.052 | 123 | 0.068 | 111.6 | 0.073 | 124 | 0.09 | 114.3 | 0.11 | 127 | 0.126 | 120.6 | 0.156 | 134 | 0.173 | 127.8 | 0.284 | 142 | 0.3
[12 empty] | 111.6 | 0.051 | 124 | 0.068 | 112.5 | 0.072 | 125 | 0.086 | 115.2 | 0.109 | 128 | 0.125 | 121.5 | 0.154 | 135 | 0.168 | 128.7 | 0.28 | 143 | 0.293
[12 empty] | 112.5 | 0.051 | 125 | 0.066 | 113.4 | 0.071 | 126 | 0.086 | 116.1 | 0.107 | 129 | 0.125 | 122.4 | 0.152 | 136 | 0.168 | 129.6 | 0.276 | 144 | 0.291
[12 empty] | 113.4 | 0.05 | 126 | 0.066 | 114.3 | 0.07 | 127 | 0.085 | 117 | 0.106 | 130 | 0.123 | 123.3 | 0.15 | 137 | 0.166 | 130.5 | 0.272 | 145 | 0.285
[12 empty] | 114.3 | 0.049 | 127 | 0.066 | 115.2 | 0.069 | 128 | 0.084 | 117.9 | 0.104 | 131 | 0.119 | 124.2 | 0.147 | 138 | 0.165 | 131.4 | 0.268 | 146 | 0.283
[12 empty] | 115.2 | 0.049 | 128 | 0.066 | 116.1 | 0.068 | 129 | 0.083 | 118.8 | 0.103 | 132 | 0.118 | 125.1 | 0.145 | 139 | 0.16 | 132.3 | 0.265 | 147 | 0.279
[12 empty] | 116.1 | 0.048 | 129 | 0.065 | 117 | 0.067 | 130 | 0.083 | 119.7 | 0.101 | 133 | 0.118 | 126 | 0.143 | 140 | 0.159 | 133.2 | 0.261 | 148 | 0.275
[12 empty] | 117 | 0.048 | 130 | 0.065 | 117.9 | 0.066 | 131 | 0.083 | 120.6 | 0.1 | 134 | 0.116 | 126.9 | 0.141 | 141 | 0.158 | 134.1 | 0.258 | 149 | 0.275
[12 empty] | 117.9 | 0.047 | 131 | 0.064 | 118.8 | 0.065 | 132 | 0.083 | 121.5 | 0.099 | 135 | 0.116 | 127.8 | 0.14 | 142 | 0.157 | 135 | 0.254 | 150 | 0.268
[12 empty] | 118.8 | 0.046 | 500 | 0.05 | 119.7 | 0.064 | 133 | 0.082 | 122.4 | 0.097 | 136 | 0.115 | 128.7 | 0.138 | 143 | 0.152 | 135.9 | 0.251 | 151 | 0.266
[12 empty] | 119.7 | 0.046 | 500 | 0.033 | 120.6 | 0.064 | 134 | 0.078 | 123.3 | 0.096 | 137 | 0.111 | 129.6 | 0.136 | 144 | 0.151 | 136.8 | 0.247 | 152 | 0.262
[12 empty] | 120.6 | 0.045 | 1000 | 0.033 | 121.5 | 0.063 | 135 | 0.078 | 124.2 | 0.095 | 138 | 0.11 | 130.5 | 0.134 | 145 | 0.15 | 137.7 | 0.244 | 153 | 0.258
[12 empty] | 121.5 | 0.045 | 6300 | 0.022 | 122.4 | 0.062 | 136 | 0.077 | 125.1 | 0.094 | 139 | 0.109 | 131.4 | 0.132 | 146 | 0.15 | 138.6 | 0.241 | 154 | 0.258
[12 empty] | 122.4 | 0.044 |  |  | 123.3 | 0.061 | 137 | 0.077 | 126 | 0.092 | 140 | 0.108 | 132.3 | 0.131 | 147 | 0.148 | 139.5 | 0.238 | 155 | 0.252
[12 empty] | 123.3 | 0.044 |  |  | 124.2 | 0.06 | 138 | 0.076 | 126.9 | 0.091 | 141 | 0.108 | 133.2 | 0.129 | 148 | 0.143 | 140.4 | 0.235 | 156 | 0.25
[12 empty] | 124.2 | 0.043 |  |  | 125.1 | 0.06 | 139 | 0.076 | 127.8 | 0.09 | 142 | 0.107 | 134.1 | 0.127 | 149 | 0.143 | 141.3 | 0.232 | 157 | 0.246
[12 empty] | 125.1 | 0.043 |  |  | 126 | 0.059 | 140 | 0.075 | 128.7 | 0.089 | 143 | 0.106 | 135 | 0.126 | 150 | 0.141 | 142.2 | 0.229 | 158 | 0.243
[12 empty] | 126 | 0.042 |  |  | 126.9 | 0.058 | 141 | 0.075 | 129.6 | 0.088 | 144 | 0.102 | 135.9 | 0.124 | 151 | 0.141 | 143.1 | 0.226 | 159 | 0.241
[12 empty] | 126.9 | 0.042 |  |  | 127.8 | 0.058 | 142 | 0.075 | 130.5 | 0.087 | 145 | 0.102 | 136.8 | 0.123 | 152 | 0.14 | 144 | 0.223 | 160 | 0.237
[12 empty] | 250.2 | 0.036 |  |  | 128.7 | 0.057 | 143 | 0.073 | 131.4 | 0.086 | 146 | 0.101 | 137.7 | 0.121 | 153 | 0.136 | 144.9 | 0.221 | 161 | 0.235
[12 empty] | 250.2 | 0.007 |  |  | 129.6 | 0.056 | 144 | 0.073 | 132.3 | 0.084 | 147 | 0.1 | 138.6 | 0.12 | 154 | 0.135 | 145.8 | 0.218 | 162 | 0.233
[12 empty] | 468 | 0.003 |  |  | 130.5 | 0.056 | 145 | 0.073 | 133.2 | 0.083 | 148 | 0.1 | 139.5 | 0.118 | 155 | 0.134 | 146.7 | 0.215 | 163 | 0.229
[12 empty] | 6300 | 0.003 |  |  | 131.4 | 0.055 | 146 | 0.069 | 134.1 | 0.082 | 149 | 0.1 | 140.4 | 0.117 | 156 | 0.133 | 147.6 | 0.213 | 164 | 0.227
[16 empty] | 132.3 | 0.054 | 147 | 0.069 | 135 | 0.081 | 150 | 0.098 | 141.3 | 0.115 | 157 | 0.133 | 148.5 | 0.21 | 165 | 0.225
[16 empty] | 133.2 | 0.054 | 148 | 0.068 | 135.9 | 0.08 | 151 | 0.098 | 142.2 | 0.114 | 158 | 0.132 | 149.4 | 0.208 | 166 | 0.225
[16 empty] | 134.1 | 0.053 | 149 | 0.068 | 136.8 | 0.08 | 152 | 0.094 | 143.1 | 0.113 | 159 | 0.127 | 150.3 | 0.205 | 167 | 0.218
[16 empty] | 135 | 0.053 | 150 | 0.068 | 137.7 | 0.079 | 153 | 0.093 | 144 | 0.111 | 160 | 0.127 | 151.2 | 0.203 | 168 | 0.216
[16 empty] | 135.9 | 0.052 | 151 | 0.068 | 138.6 | 0.078 | 154 | 0.093 | 144.9 | 0.11 | 161 | 0.126 | 152.1 | 0.2 | 169 | 0.216
[16 empty] | 136.8 | 0.051 | 152 | 0.066 | 139.5 | 0.077 | 155 | 0.093 | 145.8 | 0.109 | 162 | 0.125 | 153 | 0.198 | 170 | 0.212
[16 empty] | 137.7 | 0.051 | 153 | 0.066 | 140.4 | 0.076 | 156 | 0.091 | 146.7 | 0.107 | 163 | 0.125 | 153.9 | 0.196 | 171 | 0.21
[16 empty] | 138.6 | 0.05 | 154 | 0.066 | 141.3 | 0.075 | 157 | 0.091 | 147.6 | 0.106 | 164 | 0.123 | 154.8 | 0.193 | 172 | 0.209
[16 empty] | 139.5 | 0.05 | 155 | 0.066 | 142.2 | 0.074 | 158 | 0.091 | 148.5 | 0.105 | 165 | 0.119 | 155.7 | 0.191 | 173 | 0.208
[16 empty] | 140.4 | 0.049 | 156 | 0.066 | 143.1 | 0.073 | 159 | 0.09 | 149.4 | 0.104 | 166 | 0.118 | 156.6 | 0.189 | 174 | 0.207
[16 empty] | 141.3 | 0.049 | 157 | 0.066 | 144 | 0.073 | 160 | 0.09 | 150.3 | 0.103 | 167 | 0.118 | 157.5 | 0.187 | 175 | 0.202
[16 empty] | 142.2 | 0.048 | 158 | 0.065 | 144.9 | 0.072 | 161 | 0.086 | 151.2 | 0.102 | 168 | 0.118 | 158.4 | 0.185 | 176 | 0.201
[16 empty] | 143.1 | 0.048 | 159 | 0.065 | 145.8 | 0.071 | 162 | 0.086 | 152.1 | 0.1 | 169 | 0.116 | 159.3 | 0.183 | 177 | 0.2
[16 empty] | 144 | 0.047 | 160 | 0.065 | 146.7 | 0.07 | 163 | 0.085 | 153 | 0.099 | 170 | 0.116 | 160.2 | 0.181 | 178 | 0.198
[16 empty] | 144.9 | 0.047 | 161 | 0.061 | 147.6 | 0.069 | 164 | 0.084 | 153.9 | 0.098 | 171 | 0.115 | 161.1 | 0.179 | 179 | 0.193
[16 empty] | 145.8 | 0.046 | 162 | 0.061 | 148.5 | 0.069 | 165 | 0.084 | 154.8 | 0.097 | 172 | 0.115 | 162 | 0.177 | 180 | 0.193
[16 empty] | 146.7 | 0.046 | 163 | 0.061 | 149.4 | 0.068 | 166 | 0.084 | 155.7 | 0.096 | 173 | 0.111 | 162.9 | 0.175 | 181 | 0.191
[16 empty] | 147.6 | 0.045 | 164 | 0.06 | 150.3 | 0.067 | 167 | 0.083 | 156.6 | 0.095 | 174 | 0.11 | 163.8 | 0.173 | 182 | 0.19
[16 empty] | 148.5 | 0.045 | 165 | 0.06 | 151.2 | 0.067 | 168 | 0.083 | 157.5 | 0.094 | 175 | 0.109 | 164.7 | 0.171 | 183 | 0.186
[16 empty] | 149.4 | 0.045 | 166 | 0.06 | 152.1 | 0.066 | 169 | 0.083 | 158.4 | 0.093 | 176 | 0.109 | 165.6 | 0.169 | 184 | 0.184
[16 empty] | 150.3 | 0.044 | 167 | 0.059 | 153 | 0.065 | 170 | 0.083 | 159.3 | 0.092 | 177 | 0.108 | 166.5 | 0.168 | 185 | 0.183
[16 empty] | 151.2 | 0.044 | 168 | 0.059 | 153.9 | 0.065 | 171 | 0.082 | 160.2 | 0.091 | 178 | 0.108 | 167.4 | 0.166 | 186 | 0.183
[16 empty] | 152.1 | 0.043 | 169 | 0.059 | 154.8 | 0.064 | 172 | 0.082 | 161.1 | 0.09 | 179 | 0.108 | 168.3 | 0.164 | 187 | 0.182
[16 empty] | 153 | 0.043 | 500 | 0.05 | 155.7 | 0.063 | 173 | 0.078 | 162 | 0.089 | 180 | 0.107 | 169.2 | 0.162 | 188 | 0.177
[16 empty] | 153.9 | 0.042 | 500 | 0.033 | 156.6 | 0.063 | 174 | 0.078 | 162.9 | 0.089 | 181 | 0.102 | 170.1 | 0.161 | 189 | 0.176
[16 empty] | 154.8 | 0.042 | 1000 | 0.033 | 157.5 | 0.062 | 175 | 0.077 | 163.8 | 0.088 | 182 | 0.102 | 171 | 0.159 | 190 | 0.175
[16 empty] | 155.7 | 0.042 | 6300 | 0.022 | 158.4 | 0.061 | 176 | 0.077 | 164.7 | 0.087 | 183 | 0.102 | 171.9 | 0.158 | 191 | 0.175
[16 empty] | 250.2 | 0.038 |  |  | 159.3 | 0.061 | 177 | 0.076 | 165.6 | 0.086 | 184 | 0.101 | 172.8 | 0.156 | 192 | 0.173
[16 empty] | 250.2 | 0.007 |  |  | 160.2 | 0.06 | 178 | 0.076 | 166.5 | 0.085 | 185 | 0.101 | 173.7 | 0.154 | 193 | 0.169
[16 empty] | 468 | 0.003 |  |  | 161.1 | 0.06 | 179 | 0.076 | 167.4 | 0.084 | 186 | 0.1 | 174.6 | 0.153 | 194 | 0.168
[16 empty] | 6300 | 0.003 |  |  | 162 | 0.059 | 180 | 0.075 | 168.3 | 0.083 | 187 | 0.1 | 175.5 | 0.151 | 195 | 0.168
[20 empty] | 162.9 | 0.059 | 181 | 0.075 | 169.2 | 0.083 | 188 | 0.1 | 176.4 | 0.15 | 196 | 0.166
[20 empty] | 163.8 | 0.058 | 182 | 0.075 | 170.1 | 0.082 | 189 | 0.1 | 177.3 | 0.148 | 197 | 0.165
[20 empty] | 164.7 | 0.058 | 183 | 0.075 | 171 | 0.081 | 190 | 0.098 | 178.2 | 0.147 | 198 | 0.161
[20 empty] | 165.6 | 0.057 | 184 | 0.075 | 171.9 | 0.08 | 191 | 0.094 | 179.1 | 0.146 | 199 | 0.16
[20 empty] | 166.5 | 0.056 | 185 | 0.073 | 172.8 | 0.08 | 192 | 0.094 | 180 | 0.144 | 200 | 0.159
[20 empty] | 167.4 | 0.056 | 186 | 0.073 | 173.7 | 0.079 | 193 | 0.093 | 180.9 | 0.143 | 201 | 0.158
[20 empty] | 168.3 | 0.055 | 187 | 0.069 | 174.6 | 0.078 | 194 | 0.093 | 181.8 | 0.141 | 202 | 0.158
[20 empty] | 169.2 | 0.055 | 188 | 0.069 | 175.5 | 0.077 | 195 | 0.093 | 182.7 | 0.14 | 203 | 0.157
[20 empty] | 170.1 | 0.054 | 189 | 0.069 | 176.4 | 0.077 | 196 | 0.093 | 183.6 | 0.139 | 204 | 0.156
[20 empty] | 171 | 0.054 | 190 | 0.068 | 177.3 | 0.076 | 197 | 0.091 | 184.5 | 0.138 | 205 | 0.152
[20 empty] | 171.9 | 0.054 | 191 | 0.068 | 178.2 | 0.075 | 198 | 0.091 | 185.4 | 0.136 | 206 | 0.152
[20 empty] | 172.8 | 0.053 | 192 | 0.068 | 179.1 | 0.075 | 199 | 0.091 | 186.3 | 0.135 | 207 | 0.151
[20 empty] | 173.7 | 0.053 | 193 | 0.068 | 180 | 0.074 | 200 | 0.091 | 187.2 | 0.134 | 208 | 0.15
[20 empty] | 174.6 | 0.052 | 194 | 0.068 | 180.9 | 0.073 | 201 | 0.09 | 188.1 | 0.133 | 209 | 0.15
[20 empty] | 175.5 | 0.052 | 195 | 0.068 | 181.8 | 0.073 | 202 | 0.09 | 189 | 0.131 | 210 | 0.148
[20 empty] | 176.4 | 0.051 | 196 | 0.066 | 182.7 | 0.072 | 203 | 0.086 | 189.9 | 0.13 | 211 | 0.144
[20 empty] | 177.3 | 0.051 | 197 | 0.066 | 183.6 | 0.071 | 204 | 0.086 | 190.8 | 0.129 | 212 | 0.143
[20 empty] | 178.2 | 0.05 | 198 | 0.066 | 184.5 | 0.071 | 205 | 0.086 | 191.7 | 0.128 | 213 | 0.143
[20 empty] | 179.1 | 0.05 | 199 | 0.066 | 185.4 | 0.07 | 206 | 0.085 | 192.6 | 0.127 | 214 | 0.143
[20 empty] | 180 | 0.05 | 200 | 0.066 | 186.3 | 0.07 | 207 | 0.085 | 193.5 | 0.126 | 215 | 0.141
[20 empty] | 180.9 | 0.049 | 201 | 0.066 | 187.2 | 0.069 | 208 | 0.084 | 194.4 | 0.124 | 216 | 0.141
[20 empty] | 181.8 | 0.049 | 202 | 0.066 | 188.1 | 0.068 | 209 | 0.084 | 195.3 | 0.123 | 217 | 0.14
[20 empty] | 182.7 | 0.048 | 203 | 0.065 | 189 | 0.068 | 210 | 0.083 | 196.2 | 0.122 | 218 | 0.14
[20 empty] | 183.6 | 0.048 | 204 | 0.065 | 189.9 | 0.067 | 211 | 0.083 | 197.1 | 0.121 | 219 | 0.136
[20 empty] | 184.5 | 0.048 | 205 | 0.065 | 190.8 | 0.067 | 212 | 0.083 | 198 | 0.12 | 220 | 0.135
[20 empty] | 185.4 | 0.047 | 206 | 0.065 | 191.7 | 0.066 | 213 | 0.083 | 198.9 | 0.119 | 221 | 0.134
[20 empty] | 186.3 | 0.047 | 207 | 0.061 | 192.6 | 0.066 | 214 | 0.083 | 199.8 | 0.118 | 222 | 0.134
[20 empty] | 187.2 | 0.047 | 208 | 0.061 | 193.5 | 0.065 | 215 | 0.082 | 200.7 | 0.117 | 223 | 0.133
[20 empty] | 188.1 | 0.046 | 209 | 0.061 | 194.4 | 0.065 | 216 | 0.082 | 201.6 | 0.116 | 224 | 0.133
[20 empty] | 189 | 0.046 | 210 | 0.061 | 195.3 | 0.064 | 217 | 0.082 | 202.5 | 0.115 | 225 | 0.133
[20 empty] | 189.9 | 0.045 | 211 | 0.06 | 196.2 | 0.064 | 218 | 0.078 | 203.4 | 0.114 | 226 | 0.132
[20 empty] | 190.8 | 0.045 | 212 | 0.06 | 197.1 | 0.063 | 219 | 0.078 | 204.3 | 0.113 | 227 | 0.127
[20 empty] | 191.7 | 0.045 | 213 | 0.06 | 198 | 0.063 | 220 | 0.078 | 205.2 | 0.112 | 228 | 0.127
[20 empty] | 192.6 | 0.044 | 214 | 0.06 | 198.9 | 0.062 | 221 | 0.077 | 206.1 | 0.112 | 229 | 0.127
[20 empty] | 193.5 | 0.044 | 500 | 0.051 | 199.8 | 0.062 | 222 | 0.077 | 207 | 0.111 | 230 | 0.126
[20 empty] | 194.4 | 0.044 | 500 | 0.033 | 200.7 | 0.061 | 223 | 0.077 | 207.9 | 0.11 | 231 | 0.126
[20 empty] | 195.3 | 0.043 | 1000 | 0.033 | 201.6 | 0.061 | 224 | 0.076 | 208.8 | 0.109 | 232 | 0.125
[20 empty] | 196.2 | 0.043 | 6300 | 0.022 | 202.5 | 0.06 | 225 | 0.076 | 209.7 | 0.108 | 233 | 0.125
[20 empty] | 197.1 | 0.043 |  |  | 203.4 | 0.06 | 226 | 0.076 | 210.6 | 0.107 | 234 | 0.125
[20 empty] | 250.2 | 0.04 |  |  | 204.3 | 0.059 | 227 | 0.075 | 211.5 | 0.106 | 235 | 0.123
[20 empty] | 250.2 | 0.007 |  |  | 205.2 | 0.059 | 228 | 0.075 | 212.4 | 0.105 | 236 | 0.119
[20 empty] | 468 | 0.003 |  |  | 206.1 | 0.058 | 229 | 0.075 | 213.3 | 0.105 | 237 | 0.119
[20 empty] | 6300 | 0.003 |  |  | 207 | 0.058 | 230 | 0.075 | 214.2 | 0.104 | 238 | 0.118
[24 empty] | 207.9 | 0.058 | 231 | 0.075 | 215.1 | 0.103 | 239 | 0.118
[24 empty] | 208.8 | 0.057 | 232 | 0.075 | 216 | 0.102 | 240 | 0.118
[24 empty] | 209.7 | 0.057 | 233 | 0.073 | 216.9 | 0.101 | 241 | 0.118
[24 empty] | 210.6 | 0.056 | 234 | 0.073 | 217.8 | 0.101 | 242 | 0.116
[24 empty] | 211.5 | 0.056 | 235 | 0.073 | 218.7 | 0.1 | 243 | 0.116
[24 empty] | 212.4 | 0.056 | 236 | 0.069 | 219.6 | 0.099 | 244 | 0.116
[24 empty] | 213.3 | 0.055 | 237 | 0.069 | 220.5 | 0.098 | 245 | 0.115
[24 empty] | 214.2 | 0.055 | 238 | 0.069 | 221.4 | 0.098 | 246 | 0.115
[24 empty] | 215.1 | 0.054 | 239 | 0.069 | 222.3 | 0.097 | 247 | 0.111
[24 empty] | 216 | 0.054 | 240 | 0.068 | 223.2 | 0.096 | 248 | 0.111
[24 empty] | 216.9 | 0.054 | 241 | 0.068 | 224.1 | 0.095 | 249 | 0.11
[24 empty] | 217.8 | 0.053 | 242 | 0.068 | 225 | 0.095 | 250 | 0.11
[24 empty] | 218.7 | 0.053 | 243 | 0.068 | 225.9 | 0.094 | 251 | 0.109
[24 empty] | 219.6 | 0.053 | 244 | 0.068 | 226.8 | 0.093 | 252 | 0.109
[24 empty] | 220.5 | 0.052 | 245 | 0.068 | 227.7 | 0.093 | 253 | 0.108
[24 empty] | 221.4 | 0.052 | 246 | 0.068 | 228.6 | 0.092 | 254 | 0.108
[24 empty] | 222.3 | 0.051 | 247 | 0.068 | 229.5 | 0.091 | 255 | 0.108
[24 empty] | 223.2 | 0.051 | 248 | 0.066 | 230.4 | 0.091 | 256 | 0.108
[24 empty] | 224.1 | 0.051 | 249 | 0.066 | 231.3 | 0.09 | 257 | 0.107
[24 empty] | 225 | 0.05 | 250 | 0.066 | 232.2 | 0.089 | 258 | 0.107
[24 empty] | 225.9 | 0.05 | 251 | 0.066 | 233.1 | 0.089 | 259 | 0.106
[24 empty] | 226.8 | 0.05 | 252 | 0.066 | 234 | 0.088 | 260 | 0.102
[24 empty] | 227.7 | 0.049 | 253 | 0.066 | 234.9 | 0.088 | 261 | 0.102
[24 empty] | 228.6 | 0.049 | 254 | 0.066 | 235.8 | 0.087 | 262 | 0.102
[24 empty] | 229.5 | 0.049 | 255 | 0.066 | 236.7 | 0.086 | 263 | 0.102
[24 empty] | 230.4 | 0.048 | 256 | 0.065 | 237.6 | 0.086 | 264 | 0.101
[24 empty] | 231.3 | 0.048 | 257 | 0.065 | 238.5 | 0.085 | 265 | 0.101
[24 empty] | 232.2 | 0.048 | 258 | 0.065 | 239.4 | 0.085 | 266 | 0.1
[24 empty] | 233.1 | 0.048 | 259 | 0.065 | 240.3 | 0.084 | 267 | 0.1
[24 empty] | 234 | 0.047 | 260 | 0.065 | 241.2 | 0.083 | 268 | 0.1
[24 empty] | 234.9 | 0.047 | 261 | 0.064 | 242.1 | 0.083 | 269 | 0.1
[24 empty] | 235.8 | 0.047 | 262 | 0.061 | 243 | 0.082 | 270 | 0.1
[24 empty] | 236.7 | 0.046 | 263 | 0.061 | 243.9 | 0.082 | 271 | 0.098
[24 empty] | 237.6 | 0.046 | 264 | 0.061 | 244.8 | 0.081 | 272 | 0.098
[24 empty] | 238.5 | 0.046 | 265 | 0.061 | 245.7 | 0.081 | 273 | 0.098
[24 empty] | 239.4 | 0.046 | 266 | 0.06 | 246.6 | 0.08 | 274 | 0.094
[24 empty] | 240.3 | 0.045 | 267 | 0.06 | 247.5 | 0.08 | 275 | 0.094
[24 empty] | 241.2 | 0.045 | 268 | 0.06 | 248.4 | 0.079 | 276 | 0.094
[24 empty] | 242.1 | 0.045 | 269 | 0.06 | 249.3 | 0.079 | 277 | 0.093
[24 empty] | 243 | 0.044 | 270 | 0.06 | 250.2 | 0.078 | 278 | 0.093
[24 empty] | 243.9 | 0.044 | 271 | 0.059 | 250.2 | 0.007 | 279 | 0.093
[24 empty] | 244.8 | 0.044 | 272 | 0.059 | 468 | 0.003 | 280 | 0.093
[24 empty] | 245.7 | 0.044 | 273 | 0.059 | 6300 | 0.003 | 281 | 0.093
[24 empty] | 246.6 | 0.043 | 274 | 0.059 |  |  | 282 | 0.091
[24 empty] | 247.5 | 0.043 | 275 | 0.059 |  |  | 283 | 0.091
[24 empty] | 248.4 | 0.043 | 276 | 0.059 |  |  | 284 | 0.091
[24 empty] | 249.3 | 0.043 | 500 | 0.052 |  |  | 285 | 0.091
[24 empty] | 250.2 | 0.042 | 500 | 0.033 |  |  | 286 | 0.091
[24 empty] | 250.2 | 0.007 | 1000 | 0.033 |  |  | 287 | 0.091
[24 empty] | 468 | 0.003 | 6300 | 0.022 |  |  | 288 | 0.09
[24 empty] | 6300 | 0.003 |  |  |  |  | 289 | 0.09
[30 empty] | 290 | 0.09
[30 empty] | 291 | 0.086
[30 empty] | 292 | 0.086
[30 empty] | 293 | 0.086
[30 empty] | 294 | 0.085
[30 empty] | 295 | 0.085
[30 empty] | 296 | 0.085
[30 empty] | 297 | 0.084
[30 empty] | 298 | 0.084
[30 empty] | 300 | 0.084
[30 empty] | 300 | 0.06
[30 empty] | 500 | 0.057
[30 empty] | 500 | 0.033
[30 empty] | 1000 | 0.033
[30 empty] | 6300 | 0.022

## S&C "ST" Speed
S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter | [11 empty] | S&C VacuFuse® II Self-Resetting Interrupter
S&C "ST" Speed | [11 empty] | S&C "ST" Speed | [11 empty] | S&C "ST" Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated June 16, 2025
Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information. | [10 empty] | Tolerance: | See page 3 of S&C Information Bulletin 466-211 for tolerance information.
2ST |  |  |  | 3ST |  |  |  | 5ST |  |  |  | 7ST |  |  |  | 10ST |  |  |  | 15ST |  |  |  | 20ST
Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s | Min Trip A | Min Trip s | Total Clear A | Total Clear s
4 | 300.046 | 5 | 300.061 | 6 | 63.305 | 7 | 63.3191 | 9.9 | 45.873 | 11 | 45.89 | 13.5 | 100.535 | 15 | 100.552 | 18.9 | 1317.4346 | 21 | 1317.451 | 28.8 | 193.3662 | 32 | 193.3816 | 37.8 | 314.824 | 42 | 314.84
5 | 8.485 | 6 | 8.5 | 7 | 13.6264 | 8 | 13.6413 | 10.8 | 15.459 | 12 | 15.475 | 14.4 | 28.434 | 16 | 28.45 | 19.8 | 61.3515 | 22 | 61.366 | 29.7 | 65.6938 | 33 | 65.7101 | 38.7 | 88.666 | 43 | 88.683
6 | 3.831 | 7 | 3.846 | 8 | 7.2174 | 9 | 7.233 | 11.7 | 8.989 | 13 | 9.002 | 15.3 | 16.129 | 17 | 16.143 | 20.7 | 30.7164 | 23 | 30.733 | 30.6 | 39.0923 | 34 | 39.108 | 39.6 | 51.099 | 44 | 51.112
7 | 2.542 | 8 | 2.558 | 9 | 4.7333 | 10 | 4.7497 | 12.6 | 6.193 | 14 | 6.208 | 16.2 | 11.057 | 18 | 11.071 | 21.6 | 20.191 | 24 | 20.208 | 31.5 | 27.5911 | 35 | 27.608 | 40.5 | 35.651 | 45 | 35.666
8 | 1.914 | 9 | 1.929 | 9.9 | 3.4304 | 11 | 3.4434 | 13.5 | 4.643 | 15 | 4.658 | 17.1 | 8.3 | 19 | 8.316 | 22.5 | 14.8782 | 25 | 14.893 | 32.4 | 21.1803 | 36 | 21.1934 | 41.4 | 27.234 | 46 | 27.25
9 | 1.52 | 10 | 1.535 | 10.8 | 2.637 | 12 | 2.6518 | 14.4 | 3.664 | 16 | 3.679 | 18 | 6.574 | 20 | 6.587 | 23.4 | 11.6807 | 26 | 11.693 | 33.3 | 17.0971 | 37 | 17.1101 | 42.3 | 21.942 | 47 | 21.958
9.9 | 1.243 | 11 | 1.258 | 11.7 | 2.108 | 13 | 2.1247 | 15.3 | 2.993 | 17 | 3.008 | 18.9 | 5.395 | 21 | 5.41 | 24.3 | 9.549 | 27 | 9.566 | 34.2 | 14.2714 | 38 | 14.2851 | 43.2 | 18.308 | 48 | 18.325
10.8 | 1.044 | 12 | 1.058 | 12.6 | 1.7332 | 14 | 1.7497 | 16.2 | 2.507 | 18 | 2.525 | 19.8 | 4.541 | 22 | 4.558 | 25.2 | 8.029 | 28 | 8.043 | 35.1 | 12.2016 | 39 | 12.2163 | 44.1 | 15.661 | 49 | 15.677
11.7 | 0.889 | 13 | 0.902 | 13.5 | 1.4558 | 15 | 1.4705 | 17.1 | 2.14 | 19 | 2.154 | 20.7 | 3.897 | 23 | 3.91 | 26.1 | 6.8925 | 29 | 6.908 | 36 | 10.6215 | 40 | 10.6351 | 45 | 13.647 | 50 | 13.66
12.6 | 0.776 | 14 | 0.791 | 14.4 | 1.2436 | 16 | 1.258 | 18 | 1.855 | 20 | 1.868 | 21.6 | 3.394 | 24 | 3.408 | 27 | 6.012 | 30 | 6.027 | 36.9 | 9.3768 | 41 | 9.3913 | 45.9 | 12.065 | 51 | 12.079
13.5 | 0.686 | 15 | 0.702 | 15.3 | 1.0767 | 17 | 1.0913 | 18.9 | 1.627 | 21 | 1.641 | 22.5 | 2.992 | 25 | 3.008 | 27.9 | 5.3109 | 31 | 5.325 | 37.8 | 8.3718 | 42 | 8.3851 | 46.8 | 10.789 | 52 | 10.802
14.4 | 0.606 | 16 | 0.621 | 16.2 | 0.94297 | 18 | 0.958 | 19.8 | 1.441 | 22 | 1.458 | 23.4 | 2.664 | 26 | 2.677 | 28.8 | 4.7403 | 32 | 4.758 | 38.7 | 7.544 | 43 | 7.558 | 47.7 | 9.74 | 53 | 9.754
15.3 | 0.549 | 17 | 0.566 | 17.1 | 0.83384 | 19 | 0.84967 | 20.7 | 1.288 | 23 | 1.302 | 24.3 | 2.391 | 27 | 2.408 | 29.7 | 4.2674 | 33 | 4.283 | 39.6 | 6.8508 | 44 | 6.8663 | 48.6 | 8.862 | 54 | 8.877
16.2 | 0.493 | 18 | 0.508 | 18 | 0.74342 | 20 | 0.758 | 21.6 | 1.159 | 24 | 1.175 | 25.2 | 2.162 | 28 | 2.177 | 30.6 | 3.8697 | 34 | 3.885 | 40.5 | 6.2624 | 45 | 6.2768 | 49.5 | 8.116 | 55 | 8.133
17.1 | 0.454 | 19 | 0.468 | 18.9 | 0.66739 | 21 | 0.683 | 22.5 | 1.05 | 25 | 1.066 | 26.1 | 1.967 | 29 | 1.983 | 31.5 | 3.531 | 35 | 3.546 | 41.4 | 5.757 | 46 | 5.7747 | 50.4 | 7.476 | 56 | 7.491
18 | 0.414 | 20 | 0.429 | 19.8 | 0.60301 | 22 | 0.61634 | 23.4 | 0.956 | 26 | 0.971 | 27 | 1.799 | 30 | 1.812 | 32.4 | 3.2395 | 36 | 3.254 | 42.3 | 5.3184 | 47 | 5.333 | 51.3 | 6.921 | 57 | 6.935
18.9 | 0.383 | 21 | 0.4 | 20.7 | 0.54776 | 23 | 0.56217 | 24.3 | 0.875 | 27 | 0.891 | 27.9 | 1.653 | 31 | 1.668 | 33.3 | 2.9861 | 37 | 3 | 43.2 | 4.9346 | 48 | 4.9497 | 52.2 | 6.434 | 58 | 6.45
19.8 | 0.353 | 22 | 0.366 | 21.6 | 0.50022 | 24 | 0.51634 | 25.2 | 0.805 | 28 | 0.818 | 28.8 | 1.525 | 32 | 1.541 | 34.2 | 2.7641 | 38 | 2.779 | 44.1 | 4.5959 | 49 | 4.6101 | 53.1 | 6.005 | 59 | 6.018
20.7 | 0.328 | 23 | 0.341 | 22.5 | 0.45872 | 25 | 0.47467 | 26.1 | 0.743 | 29 | 0.758 | 29.7 | 1.413 | 33 | 1.427 | 35.1 | 2.5682 | 39 | 2.583 | 45 | 4.2952 | 50 | 4.3101 | 54 | 5.623 | 60 | 5.637
21.6 | 0.306 | 24 | 0.321 | 23.4 | 0.42246 | 26 | 0.43509 | 27 | 0.688 | 30 | 0.702 | 30.6 | 1.313 | 34 | 1.327 | 36 | 2.3942 | 40 | 2.408 | 45.9 | 4.0265 | 51 | 4.0413 | 54.9 | 5.282 | 61 | 5.3
22.5 | 0.285 | 25 | 0.3 | 24.3 | 0.39049 | 27 | 0.40384 | 27.9 | 0.64 | 31 | 0.654 | 31.5 | 1.224 | 35 | 1.241 | 36.9 | 2.2387 | 41 | 2.252 | 46.8 | 3.7851 | 52 | 3.7997 | 55.8 | 4.975 | 62 | 4.991
23.4 | 0.268 | 26 | 0.283 | 25.2 | 0.3621 | 28 | 0.37675 | 28.8 | 0.596 | 32 | 0.61 | 32.4 | 1.145 | 36 | 1.16 | 37.8 | 2.0992 | 42 | 2.116 | 47.7 | 3.5672 | 53 | 3.583 | 56.7 | 4.698 | 63 | 4.712
24.3 | 0.252 | 27 | 0.266 | 26.1 | 0.33686 | 29 | 0.35175 | 29.7 | 0.557 | 33 | 0.571 | 33.3 | 1.073 | 37 | 1.087 | 38.7 | 1.9733 | 43 | 1.987 | 48.6 | 3.3696 | 54 | 3.383 | 57.6 | 4.447 | 64 | 4.46
25.2 | 0.236 | 28 | 0.25 | 27 | 0.31423 | 30 | 0.32884 | 30.6 | 0.522 | 34 | 0.535 | 34.2 | 1.008 | 38 | 1.025 | 39.6 | 1.8592 | 44 | 1.875 | 49.5 | 3.1897 | 55 | 3.2038 | 58.5 | 4.217 | 65 | 4.233
26.1 | 0.224 | 29 | 0.241 | 27.9 | 0.29398 | 31 | 0.308 | 31.5 | 0.49 | 35 | 0.504 | 35.1 | 0.95 | 39 | 0.966 | 40.5 | 1.7555 | 45 | 1.768 | 50.4 | 3.0252 | 56 | 3.0413 | 59.4 | 4.007 | 66 | 4.025
27 | 0.212 | 30 | 0.227 | 28.8 | 0.27565 | 32 | 0.29134 | 32.4 | 0.462 | 36 | 0.477 | 36 | 0.896 | 40 | 0.91 | 41.4 | 1.6607 | 46 | 1.675 | 51.3 | 2.8744 | 57 | 2.8913 | 60.3 | 3.815 | 67 | 3.829
27.9 | 0.201 | 31 | 0.216 | 29.7 | 0.25907 | 33 | 0.27467 | 33.3 | 0.435 | 37 | 0.45 | 36.9 | 0.847 | 41 | 0.86 | 42.3 | 1.5741 | 47 | 1.587 | 52.2 | 2.7356 | 58 | 2.7497 | 61.2 | 3.637 | 68 | 3.652
28.8 | 0.192 | 32 | 0.208 | 30.6 | 0.24395 | 34 | 0.258 | 34.2 | 0.412 | 38 | 0.427 | 37.8 | 0.802 | 42 | 0.816 | 43.2 | 1.4943 | 48 | 1.508 | 53.1 | 2.6076 | 59 | 2.6247 | 62.1 | 3.473 | 69 | 3.487
29.7 | 0.183 | 33 | 0.2 | 31.5 | 0.23031 | 35 | 0.24342 | 35.1 | 0.39 | 39 | 0.404 | 38.7 | 0.761 | 43 | 0.775 | 44.1 | 1.4209 | 49 | 1.435 | 54 | 2.4892 | 60 | 2.5038 | 63 | 3.321 | 70 | 3.335
30.6 | 0.174 | 34 | 0.191 | 32.4 | 0.21779 | 36 | 0.233 | 36 | 0.369 | 40 | 0.383 | 39.6 | 0.723 | 44 | 0.737 | 45 | 1.3531 | 50 | 1.368 | 54.9 | 2.3794 | 61 | 2.3934 | 63.9 | 3.18 | 71 | 3.193
31.5 | 0.167 | 35 | 0.183 | 33.3 | 0.20633 | 37 | 0.2205 | 36.9 | 0.351 | 41 | 0.366 | 40.5 | 0.688 | 45 | 0.702 | 45.9 | 1.2904 | 51 | 1.304 | 55.8 | 2.2773 | 62 | 2.2913 | 64.8 | 3.049 | 72 | 3.066
32.4 | 0.16 | 36 | 0.176 | 34.2 | 0.19577 | 38 | 0.21009 | 37.8 | 0.334 | 42 | 0.35 | 41.4 | 0.656 | 46 | 0.671 | 46.8 | 1.2321 | 52 | 1.246 | 56.7 | 2.1821 | 63 | 2.1955 | 65.7 | 2.927 | 73 | 2.941
33.3 | 0.154 | 37 | 0.168 | 35.1 | 0.18578 | 39 | 0.20106 | 38.7 | 0.318 | 43 | 0.333 | 42.3 | 0.626 | 47 | 0.641 | 47.7 | 1.178 | 53 | 1.191 | 57.6 | 2.0933 | 64 | 2.108 | 66.6 | 2.812 | 74 | 2.827
34.2 | 0.147 | 38 | 0.164 | 36 | 0.17679 | 40 | 0.19273 | 39.6 | 0.303 | 44 | 0.318 | 43.2 | 0.598 | 48 | 0.612 | 48.6 | 1.1275 | 54 | 1.141 | 58.5 | 2.0102 | 65 | 2.0247 | 67.5 | 2.705 | 75 | 2.718
35.1 | 0.142 | 39 | 0.158 | 36.9 | 0.16848 | 41 | 0.18439 | 40.5 | 0.29 | 45 | 0.304 | 44.1 | 0.572 | 49 | 0.585 | 49.5 | 1.0804 | 55 | 1.093 | 59.4 | 1.9324 | 66 | 1.9455 | 68.4 | 2.604 | 76 | 2.618
36 | 0.137 | 40 | 0.152 | 37.8 | 0.1608 | 42 | 0.17606 | 41.4 | 0.277 | 46 | 0.291 | 45 | 0.547 | 50 | 0.56 | 50.4 | 1.0364 | 56 | 1.05 | 60.3 | 1.8593 | 67 | 1.8747 | 69.3 | 2.51 | 77 | 2.525
36.9 | 0.132 | 41 | 0.148 | 38.7 | 0.15368 | 43 | 0.16842 | 42.3 | 0.265 | 47 | 0.279 | 45.9 | 0.524 | 51 | 0.541 | 51.3 | 0.99505 | 57 | 1.01 | 61.2 | 1.7905 | 68 | 1.8038 | 70.2 | 2.421 | 78 | 2.435
37.8 | 0.127 | 42 | 0.143 | 39.6 | 0.147 | 44 | 0.16078 | 43.2 | 0.254 | 48 | 0.268 | 46.8 | 0.503 | 52 | 0.518 | 52.2 | 0.9563 | 58 | 0.971 | 62.1 | 1.7259 | 69 | 1.7413 | 71.1 | 2.337 | 79 | 2.352
38.7 | 0.123 | 43 | 0.14 | 40.5 | 0.14085 | 45 | 0.158 | 44.1 | 0.244 | 49 | 0.258 | 47.7 | 0.483 | 53 | 0.5 | 53.1 | 0.91991 | 59 | 0.935 | 63 | 1.6648 | 70 | 1.6788 | 72 | 2.258 | 80 | 2.275
39.6 | 0.119 | 44 | 0.134 | 41.4 | 0.13502 | 46 | 0.15106 | 45 | 0.234 | 50 | 0.25 | 48.6 | 0.465 | 54 | 0.479 | 54 | 0.88563 | 60 | 0.9 | 63.9 | 1.6072 | 71 | 1.6205 | 72.9 | 2.183 | 81 | 2.2
40.5 | 0.115 | 45 | 0.133 | 42.3 | 0.12964 | 47 | 0.14412 | 45.9 | 0.225 | 51 | 0.241 | 49.5 | 0.447 | 55 | 0.46 | 54.9 | 0.85334 | 61 | 0.868 | 64.8 | 1.5527 | 72 | 1.5663 | 73.8 | 2.112 | 82 | 2.127
41.4 | 0.112 | 46 | 0.127 | 43.2 | 0.12454 | 48 | 0.14134 | 46.8 | 0.216 | 52 | 0.233 | 50.4 | 0.43 | 56 | 0.443 | 55.8 | 0.82286 | 62 | 0.837 | 65.7 | 1.5012 | 73 | 1.5163 | 74.7 | 2.045 | 83 | 2.058
42.3 | 0.108 | 47 | 0.125 | 44.1 | 0.11981 | 49 | 0.13508 | 47.7 | 0.208 | 53 | 0.225 | 51.3 | 0.415 | 57 | 0.429 | 56.7 | 0.79405 | 63 | 0.808 | 66.6 | 1.4523 | 74 | 1.4663 | 75.6 | 1.981 | 84 | 1.996
43.2 | 0.105 | 48 | 0.119 | 45 | 0.11532 | 50 | 0.133 | 48.6 | 0.201 | 54 | 0.216 | 52.2 | 0.4 | 58 | 0.416 | 57.6 | 0.7668 | 64 | 0.783 | 67.5 | 1.406 | 75 | 1.4205 | 76.5 | 1.92 | 85 | 1.935
44.1 | 0.102 | 49 | 0.118 | 45.9 | 0.11116 | 51 | 0.12606 | 49.5 | 0.194 | 55 | 0.208 | 53.1 | 0.386 | 59 | 0.4 | 58.5 | 0.74097 | 65 | 0.758 | 68.4 | 1.3619 | 76 | 1.3768 | 77.4 | 1.863 | 86 | 1.877
45 | 0.099 | 50 | 0.116 | 46.8 | 0.10718 | 52 | 0.12467 | 50.4 | 0.186 | 56 | 0.202 | 54 | 0.373 | 60 | 0.387 | 59.4 | 0.71654 | 66 | 0.733 | 69.3 | 1.32 | 77 | 1.3351 | 78.3 | 1.808 | 87 | 1.825
45.9 | 0.096 | 51 | 0.111 | 47.7 | 0.10346 | 53 | 0.11841 | 51.3 | 0.18 | 57 | 0.194 | 54.9 | 0.36 | 61 | 0.375 | 60.3 | 0.69329 | 67 | 0.708 | 70.2 | 1.2801 | 78 | 1.2934 | 79.2 | 1.756 | 88 | 1.768
46.8 | 0.094 | 52 | 0.109 | 48.6 | 0.099966 | 54 | 0.11634 | 52.2 | 0.174 | 58 | 0.191 | 55.8 | 0.348 | 62 | 0.362 | 61.2 | 0.67123 | 68 | 0.685 | 71.1 | 1.2421 | 79 | 1.258 | 80.1 | 1.706 | 89 | 1.718
47.7 | 0.091 | 53 | 0.108 | 49.5 | 0.096599 | 55 | 0.11079 | 53.1 | 0.168 | 59 | 0.184 | 56.7 | 0.337 | 63 | 0.352 | 62.1 | 0.65026 | 69 | 0.666 | 72 | 1.2059 | 80 | 1.2205 | 81 | 1.658 | 90 | 1.675
48.6 | 0.088 | 54 | 0.102 | 50.4 | 0.093462 | 56 | 0.1094 | 54 | 0.163 | 60 | 0.177 | 57.6 | 0.326 | 64 | 0.341 | 63 | 0.63028 | 70 | 0.643 | 72.9 | 1.1713 | 81 | 1.1851 | 81.9 | 1.612 | 91 | 1.627
49.5 | 0.086 | 55 | 0.101 | 51.3 | 0.090491 | 57 | 0.108 | 54.9 | 0.158 | 61 | 0.175 | 58.5 | 0.316 | 65 | 0.333 | 63.9 | 0.61128 | 71 | 0.625 | 73.8 | 1.1383 | 82 | 1.1518 | 82.8 | 1.569 | 92 | 1.583
50.4 | 0.084 | 56 | 0.1 | 52.2 | 0.087671 | 58 | 0.10243 | 55.8 | 0.153 | 62 | 0.168 | 59.4 | 0.306 | 66 | 0.321 | 64.8 | 0.59313 | 72 | 0.608 | 74.7 | 1.1067 | 83 | 1.1205 | 83.7 | 1.527 | 93 | 1.541
51.3 | 0.082 | 57 | 0.1 | 53.1 | 0.084997 | 59 | 0.10105 | 56.7 | 0.148 | 63 | 0.165 | 60.3 | 0.297 | 67 | 0.31 | 65.7 | 0.57583 | 73 | 0.591 | 75.6 | 1.0765 | 84 | 1.0913 | 84.6 | 1.487 | 94 | 1.502
52.2 | 0.081 | 58 | 0.098 | 54 | 0.082479 | 60 | 0.099673 | 57.6 | 0.144 | 64 | 0.159 | 61.2 | 0.288 | 68 | 0.302 | 66.6 | 0.55931 | 74 | 0.575 | 76.5 | 1.0476 | 85 | 1.0622 | 85.5 | 1.449 | 95 | 1.462
53.1 | 0.079 | 59 | 0.093 | 54.9 | 0.080031 | 61 | 0.09414 | 58.5 | 0.14 | 65 | 0.157 | 62.1 | 0.28 | 69 | 0.293 | 67.5 | 0.54354 | 75 | 0.558 | 77.4 | 1.0199 | 86 | 1.0351 | 86.4 | 1.412 | 96 | 1.427
54 | 0.077 | 60 | 0.093 | 55.8 | 0.077757 | 62 | 0.092739 | 59.4 | 0.136 | 66 | 0.151 | 63 | 0.272 | 70 | 0.285 | 68.4 | 0.52841 | 76 | 0.543 | 78.3 | 0.99327 | 87 | 1.008 | 87.3 | 1.377 | 97 | 1.391
54.9 | 0.075 | 61 | 0.091 | 56.7 | 0.07553 | 63 | 0.091332 | 60.3 | 0.132 | 67 | 0.148 | 63.9 | 0.264 | 71 | 0.279 | 69.3 | 0.51396 | 77 | 0.527 | 79.2 | 0.96779 | 88 | 0.983 | 88.2 | 1.343 | 98 | 1.358
55.8 | 0.073 | 62 | 0.09 | 57.6 | 0.073462 | 64 | 0.089925 | 61.2 | 0.128 | 68 | 0.143 | 64.8 | 0.257 | 72 | 0.271 | 70.2 | 0.50008 | 78 | 0.516 | 80.1 | 0.94332 | 89 | 0.958 | 89.1 | 1.311 | 99 | 1.325
56.7 | 0.072 | 63 | 0.086 | 58.5 | 0.071491 | 65 | 0.085744 | 62.1 | 0.125 | 69 | 0.141 | 65.7 | 0.25 | 73 | 0.266 | 71.1 | 0.48682 | 79 | 0.502 | 81 | 0.91981 | 90 | 0.93509 | 90 | 1.279 | 100 | 1.293
57.6 | 0.07 | 64 | 0.085 | 59.4 | 0.069594 | 66 | 0.085057 | 63 | 0.121 | 70 | 0.136 | 66.6 | 0.243 | 74 | 0.258 | 72 | 0.47409 | 80 | 0.491 | 81.9 | 0.89725 | 91 | 0.91009 | 90.9 | 1.249 | 101 | 1.266
58.5 | 0.069 | 65 | 0.084 | 60.3 | 0.067798 | 67 | 0.08301 | 63.9 | 0.118 | 71 | 0.133 | 67.5 | 0.237 | 75 | 0.252 | 72.9 | 0.46185 | 81 | 0.477 | 82.8 | 0.87549 | 92 | 0.89134 | 91.8 | 1.22 | 102 | 1.235
59.4 | 0.067 | 66 | 0.083 | 61.2 | 0.066095 | 68 | 0.08301 | 64.8 | 0.115 | 72 | 0.132 | 68.4 | 0.231 | 76 | 0.243 | 73.8 | 0.45011 | 82 | 0.466 | 83.7 | 0.85458 | 93 | 0.86842 | 92.7 | 1.192 | 103 | 1.208
60.3 | 0.066 | 67 | 0.083 | 62.1 | 0.064419 | 69 | 0.081649 | 65.7 | 0.112 | 73 | 0.127 | 69.3 | 0.225 | 77 | 0.241 | 74.7 | 0.43886 | 83 | 0.452 | 84.6 | 0.83445 | 94 | 0.84967 | 93.6 | 1.165 | 104 | 1.179
61.2 | 0.064 | 68 | 0.082 | 63 | 0.062801 | 70 | 0.077503 | 66.6 | 0.109 | 74 | 0.125 | 70.2 | 0.219 | 78 | 0.233 | 75.6 | 0.42802 | 84 | 0.441 | 85.5 | 0.81503 | 95 | 0.82884 | 94.5 | 1.139 | 105 | 1.154
62.1 | 0.063 | 69 | 0.078 | 63.9 | 0.061335 | 71 | 0.076797 | 67.5 | 0.106 | 75 | 0.123 | 71.1 | 0.213 | 79 | 0.227 | 76.5 | 0.4176 | 85 | 0.433 | 86.4 | 0.79631 | 96 | 0.81009 | 95.4 | 1.114 | 106 | 1.127
63 | 0.062 | 70 | 0.077 | 64.8 | 0.059852 | 72 | 0.076088 | 68.4 | 0.104 | 76 | 0.118 | 72 | 0.208 | 80 | 0.225 | 77.4 | 0.40756 | 86 | 0.425 | 87.3 | 0.77828 | 97 | 0.79342 | 96.3 | 1.09 | 107 | 1.104
63.9 | 0.061 | 71 | 0.076 | 65.7 | 0.058459 | 73 | 0.074661 | 69.3 | 0.101 | 77 | 0.118 | 72.9 | 0.203 | 81 | 0.218 | 78.3 | 0.39787 | 87 | 0.412 | 88.2 | 0.76087 | 98 | 0.77467 | 97.2 | 1.067 | 108 | 1.083
64.8 | 0.06 | 72 | 0.075 | 66.6 | 0.057112 | 74 | 0.07466 | 70.2 | 0.099 | 78 | 0.116 | 73.8 | 0.198 | 82 | 0.212 | 79.2 | 0.38859 | 88 | 0.402 | 89.1 | 0.74407 | 99 | 0.758 | 98.1 | 1.044 | 109 | 1.058
65.7 | 0.058 | 73 | 0.075 | 67.5 | 0.055836 | 75 | 0.073231 | 71.1 | 0.097 | 79 | 0.111 | 74.7 | 0.194 | 83 | 0.208 | 80.1 | 0.37962 | 89 | 0.393 | 90 | 0.72783 | 100 | 0.74134 | 99 | 1.022 | 110 | 1.035
66.6 | 0.057 | 74 | 0.075 | 68.4 | 0.054596 | 76 | 0.069033 | 72 | 0.094 | 80 | 0.109 | 75.6 | 0.189 | 84 | 0.207 | 81 | 0.37096 | 90 | 0.385 | 90.9 | 0.71216 | 101 | 0.72675 | 99.9 | 1.001 | 111 | 1.016
67.5 | 0.056 | 75 | 0.073 | 69.3 | 0.053411 | 77 | 0.068355 | 72.9 | 0.092 | 81 | 0.108 | 76.5 | 0.185 | 85 | 0.2 | 81.9 | 0.36266 | 91 | 0.377 | 91.8 | 0.69698 | 102 | 0.71009 | 100.8 | 0.981 | 112 | 0.993
68.4 | 0.055 | 76 | 0.069 | 70.2 | 0.05229 | 78 | 0.067683 | 73.8 | 0.09 | 82 | 0.108 | 77.4 | 0.18 | 86 | 0.194 | 82.8 | 0.35458 | 92 | 0.368 | 92.7 | 0.68232 | 103 | 0.69967 | 101.7 | 0.961 | 113 | 0.975
69.3 | 0.054 | 77 | 0.069 | 71.1 | 0.051178 | 79 | 0.066351 | 74.7 | 0.088 | 83 | 0.102 | 78.3 | 0.176 | 87 | 0.193 | 83.7 | 0.34681 | 93 | 0.36 | 93.6 | 0.66816 | 104 | 0.683 | 102.6 | 0.942 | 114 | 0.958
70.2 | 0.053 | 78 | 0.068 | 72 | 0.050146 | 80 | 0.066351 | 75.6 | 0.086 | 84 | 0.102 | 79.2 | 0.172 | 88 | 0.19 | 84.6 | 0.3393 | 94 | 0.354 | 94.5 | 0.65443 | 105 | 0.66842 | 103.5 | 0.923 | 115 | 0.937
71.1 | 0.053 | 79 | 0.068 | 72.9 | 0.049119 | 81 | 0.066351 | 76.5 | 0.085 | 85 | 0.1 | 80.1 | 0.169 | 89 | 0.184 | 85.5 | 0.33204 | 95 | 0.346 | 95.4 | 0.64115 | 106 | 0.658 | 104.4 | 0.905 | 116 | 0.918
72 | 0.052 | 80 | 0.068 | 73.8 | 0.048145 | 82 | 0.065023 | 77.4 | 0.083 | 86 | 0.1 | 81 | 0.165 | 90 | 0.182 | 86.4 | 0.32501 | 96 | 0.341 | 96.3 | 0.62829 | 107 | 0.64342 | 105.3 | 0.888 | 117 | 0.902
72.9 | 0.051 | 81 | 0.066 | 74.7 | 0.047199 | 83 | 0.065023 | 78.3 | 0.081 | 87 | 0.098 | 81.9 | 0.162 | 91 | 0.177 | 87.3 | 0.31822 | 97 | 0.333 | 97.2 | 0.61582 | 108 | 0.633 | 106.2 | 0.871 | 118 | 0.885
73.8 | 0.05 | 82 | 0.066 | 75.6 | 0.046281 | 84 | 0.060901 | 79.2 | 0.079 | 88 | 0.094 | 82.8 | 0.158 | 92 | 0.175 | 88.2 | 0.31165 | 98 | 0.327 | 98.1 | 0.60374 | 109 | 0.61842 | 107.1 | 0.854 | 119 | 0.868
74.7 | 0.049 | 83 | 0.066 | 76.5 | 0.045429 | 85 | 0.060182 | 80.1 | 0.078 | 89 | 0.093 | 83.7 | 0.155 | 93 | 0.169 | 89.1 | 0.30529 | 99 | 0.318 | 99 | 0.59203 | 110 | 0.608 | 108 | 0.838 | 120 | 0.852
75.6 | 0.049 | 84 | 0.066 | 77.4 | 0.044578 | 500 | 0.048 | 81 | 0.076 | 90 | 0.091 | 84.6 | 0.152 | 94 | 0.168 | 90 | 0.29912 | 100 | 0.316 | 99.9 | 0.58067 | 111 | 0.59342 | 108.9 | 0.823 | 121 | 0.837
76.5 | 0.048 | 85 | 0.065 | 78.3 | 0.043735 | 500 | 0.033 | 81.9 | 0.075 | 91 | 0.091 | 85.5 | 0.149 | 95 | 0.166 | 90.9 | 0.29315 | 101 | 0.308 | 100.8 | 0.56964 | 112 | 0.583 | 109.8 | 0.808 | 122 | 0.825
77.4 | 0.047 | 86 | 0.065 | 79.2 | 0.04298 | 1000 | 0.033 | 82.8 | 0.073 | 92 | 0.09 | 86.4 | 0.146 | 96 | 0.161 | 91.8 | 0.28735 | 102 | 0.302 | 101.7 | 0.55896 | 113 | 0.57467 | 110.7 | 0.793 | 123 | 0.808
78.3 | 0.046 | 87 | 0.061 | 80.1 | 0.042243 | 6300 | 0.022 | 83.7 | 0.072 | 93 | 0.086 | 87.3 | 0.143 | 97 | 0.158 | 92.7 | 0.28174 | 103 | 0.296 | 102.6 | 0.54857 | 114 | 0.56217 | 111.6 | 0.779 | 124 | 0.793
79.2 | 0.046 | 88 | 0.061 | 250.2 | 0.034831 |  |  | 84.6 | 0.071 | 94 | 0.085 | 88.2 | 0.14 | 98 | 0.157 | 93.6 | 0.27632 | 104 | 0.291 | 103.5 | 0.53846 | 115 | 0.55175 | 112.5 | 0.765 | 125 | 0.779
80.1 | 0.045 | 89 | 0.06 | 250.2 | 0.0072687 |  |  | 85.5 | 0.069 | 95 | 0.084 | 89.1 | 0.137 | 99 | 0.152 | 94.5 | 0.27105 | 105 | 0.285 | 104.4 | 0.52866 | 116 | 0.54342 | 113.4 | 0.752 | 126 | 0.766
81 | 0.044 | 90 | 0.059 | 468 | 0.003 |  |  | 86.4 | 0.068 | 96 | 0.084 | 90 | 0.135 | 100 | 0.151 | 95.4 | 0.26594 | 106 | 0.283 | 105.3 | 0.51913 | 117 | 0.533 | 114.3 | 0.739 | 127 | 0.752
81.9 | 0.044 | 91 | 0.059 | 6300 | 0.003 |  |  | 87.3 | 0.067 | 97 | 0.083 | 90.9 | 0.132 | 101 | 0.15 | 96.3 | 0.26098 | 107 | 0.275 | 106.2 | 0.50986 | 118 | 0.52467 | 115.2 | 0.726 | 128 | 0.741
82.8 | 0.043 | 92 | 0.059 |  |  |  |  | 88.2 | 0.066 | 98 | 0.083 | 91.8 | 0.13 | 102 | 0.144 | 97.2 | 0.25616 | 108 | 0.271 | 107.1 | 0.50085 | 119 | 0.51634 | 116.1 | 0.714 | 129 | 0.727
83.7 | 0.043 | 93 | 0.058 |  |  |  |  | 89.1 | 0.065 | 99 | 0.082 | 92.7 | 0.127 | 103 | 0.143 | 98.1 | 0.25148 | 109 | 0.266 | 108 | 0.49209 | 120 | 0.508 | 117 | 0.702 | 130 | 0.716
84.6 | 0.042 | 94 | 0.058 |  |  |  |  | 90 | 0.063 | 100 | 0.078 | 93.6 | 0.125 | 104 | 0.141 | 99 | 0.24693 | 110 | 0.26 | 108.9 | 0.48356 | 121 | 0.49967 | 117.9 | 0.69 | 131 | 0.704
85.5 | 0.042 | 500 | 0.048 |  |  |  |  | 90.9 | 0.062 | 101 | 0.077 | 94.5 | 0.123 | 105 | 0.14 | 99.9 | 0.24252 | 111 | 0.258 | 109.8 | 0.47527 | 122 | 0.49134 | 118.8 | 0.679 | 132 | 0.693
86.4 | 0.041 | 500 | 0.033 |  |  |  |  | 91.8 | 0.061 | 102 | 0.077 | 95.4 | 0.121 | 106 | 0.135 | 100.8 | 0.23822 | 112 | 0.252 | 110.7 | 0.46722 | 123 | 0.483 | 119.7 | 0.667 | 133 | 0.683
160.2 | 0.036 | 1000 | 0.033 |  |  |  |  | 92.7 | 0.06 | 103 | 0.076 | 96.3 | 0.119 | 107 | 0.134 | 101.7 | 0.23406 | 113 | 0.25 | 111.6 | 0.45936 | 124 | 0.47467 | 120.6 | 0.657 | 134 | 0.671
250.2 | 0.035 | 6300 | 0.022 |  |  |  |  | 93.6 | 0.059 | 104 | 0.075 | 97.2 | 0.117 | 108 | 0.133 | 102.6 | 0.23 | 114 | 0.243 | 112.5 | 0.4517 | 125 | 0.46634 | 121.5 | 0.646 | 135 | 0.66
250.2 | 0.007 | [6 empty] | 94.5 | 0.058 | 105 | 0.075 | 98.1 | 0.115 | 109 | 0.132 | 103.5 | 0.22604 | 115 | 0.241 | 113.4 | 0.44424 | 126 | 0.458 | 122.4 | 0.636 | 136 | 0.65
468 | 0.003 | [6 empty] | 95.4 | 0.057 | 106 | 0.075 | 99 | 0.113 | 110 | 0.127 | 104.4 | 0.22219 | 116 | 0.235 | 114.3 | 0.43697 | 127 | 0.45175 | 123.3 | 0.626 | 137 | 0.641
6300 | 0.003 | [6 empty] | 96.3 | 0.056 | 107 | 0.073 | 99.9 | 0.111 | 111 | 0.126 | 105.3 | 0.21846 | 117 | 0.233 | 115.2 | 0.4299 | 128 | 0.44342 | 124.2 | 0.616 | 138 | 0.633
[8 empty] | 97.2 | 0.056 | 108 | 0.073 | 100.8 | 0.109 | 112 | 0.125 | 106.2 | 0.2148 | 118 | 0.229 | 116.1 | 0.42298 | 129 | 0.43717 | 125.1 | 0.606 | 139 | 0.621
[8 empty] | 98.1 | 0.055 | 109 | 0.069 | 101.7 | 0.107 | 113 | 0.125 | 107.1 | 0.21125 | 119 | 0.225 | 117 | 0.41625 | 130 | 0.433 | 126 | 0.597 | 140 | 0.61
[8 empty] | 99 | 0.054 | 110 | 0.068 | 102.6 | 0.105 | 114 | 0.119 | 108 | 0.20779 | 120 | 0.225 | 117.9 | 0.40968 | 131 | 0.42467 | 126.9 | 0.588 | 141 | 0.602
[8 empty] | 99.9 | 0.053 | 111 | 0.068 | 103.5 | 0.104 | 115 | 0.118 | 108.9 | 0.20442 | 121 | 0.218 | 118.8 | 0.40329 | 132 | 0.41842 | 127.8 | 0.579 | 142 | 0.593
[8 empty] | 100.8 | 0.052 | 112 | 0.068 | 104.4 | 0.102 | 116 | 0.118 | 109.8 | 0.20113 | 122 | 0.216 | 119.7 | 0.39703 | 133 | 0.41009 | 128.7 | 0.57 | 143 | 0.585
[8 empty] | 101.7 | 0.052 | 113 | 0.068 | 105.3 | 0.1 | 117 | 0.116 | 110.7 | 0.19795 | 123 | 0.212 | 120.6 | 0.39092 | 134 | 0.408 | 129.6 | 0.562 | 144 | 0.577
[8 empty] | 102.6 | 0.051 | 114 | 0.066 | 106.2 | 0.099 | 118 | 0.116 | 111.6 | 0.19485 | 124 | 0.21 | 121.5 | 0.38496 | 135 | 0.39967 | 130.5 | 0.554 | 145 | 0.568
[8 empty] | 103.5 | 0.05 | 115 | 0.066 | 107.1 | 0.097 | 119 | 0.115 | 112.5 | 0.19149 | 125 | 0.208 | 122.4 | 0.37915 | 136 | 0.39342 | 131.4 | 0.546 | 146 | 0.56
[8 empty] | 104.4 | 0.049 | 116 | 0.066 | 108 | 0.096 | 120 | 0.111 | 113.4 | 0.18853 | 126 | 0.202 | 123.3 | 0.37347 | 137 | 0.38717 | 132.3 | 0.538 | 147 | 0.552
[8 empty] | 105.3 | 0.049 | 117 | 0.066 | 108.9 | 0.094 | 121 | 0.109 | 114.3 | 0.18564 | 127 | 0.201 | 124.2 | 0.36793 | 138 | 0.383 | 133.2 | 0.53 | 148 | 0.543
[8 empty] | 106.2 | 0.048 | 118 | 0.065 | 109.8 | 0.093 | 122 | 0.108 | 115.2 | 0.18281 | 128 | 0.2 | 125.1 | 0.36251 | 139 | 0.37675 | 134.1 | 0.522 | 149 | 0.535
[8 empty] | 107.1 | 0.047 | 119 | 0.065 | 110.7 | 0.092 | 123 | 0.108 | 116.1 | 0.18005 | 129 | 0.194 | 126 | 0.3572 | 140 | 0.37467 | 135 | 0.515 | 150 | 0.529
[8 empty] | 108 | 0.047 | 120 | 0.061 | 111.6 | 0.09 | 124 | 0.107 | 117 | 0.17737 | 130 | 0.193 | 126.9 | 0.35205 | 141 | 0.36634 | 135.9 | 0.508 | 151 | 0.525
[8 empty] | 108.9 | 0.046 | 121 | 0.061 | 112.5 | 0.089 | 125 | 0.107 | 117.9 | 0.17476 | 131 | 0.191 | 127.8 | 0.34697 | 142 | 0.36009 | 136.8 | 0.501 | 152 | 0.516
[8 empty] | 109.8 | 0.045 | 122 | 0.06 | 113.4 | 0.088 | 126 | 0.102 | 118.8 | 0.17218 | 132 | 0.189 | 128.7 | 0.34205 | 143 | 0.358 | 137.7 | 0.494 | 153 | 0.508
[8 empty] | 110.7 | 0.045 | 123 | 0.06 | 114.3 | 0.086 | 127 | 0.102 | 119.7 | 0.16966 | 133 | 0.185 | 129.6 | 0.33719 | 144 | 0.35175 | 138.6 | 0.487 | 154 | 0.502
[8 empty] | 111.6 | 0.044 | 500 | 0.05 | 115.2 | 0.085 | 128 | 0.101 | 120.6 | 0.16723 | 134 | 0.183 | 130.5 | 0.33248 | 145 | 0.34967 | 139.5 | 0.48 | 155 | 0.493
[8 empty] | 112.5 | 0.044 | 500 | 0.033 | 116.1 | 0.084 | 129 | 0.1 | 121.5 | 0.16482 | 135 | 0.182 | 131.4 | 0.32783 | 146 | 0.34134 | 140.4 | 0.474 | 156 | 0.491
[8 empty] | 113.4 | 0.043 | 1000 | 0.033 | 117 | 0.083 | 130 | 0.1 | 122.4 | 0.16252 | 136 | 0.177 | 132.3 | 0.32333 | 147 | 0.33717 | 141.3 | 0.468 | 157 | 0.483
[8 empty] | 114.3 | 0.043 | 6300 | 0.022 | 117.9 | 0.082 | 131 | 0.098 | 123.3 | 0.16021 | 137 | 0.176 | 133.2 | 0.31888 | 148 | 0.333 | 142.2 | 0.461 | 158 | 0.475
[8 empty] | 115.2 | 0.042 |  |  | 118.8 | 0.081 | 132 | 0.098 | 124.2 | 0.15798 | 138 | 0.175 | 134.1 | 0.31456 | 149 | 0.32884 | 143.1 | 0.455 | 159 | 0.468
[8 empty] | 116.1 | 0.042 |  |  | 119.7 | 0.079 | 133 | 0.094 | 125.1 | 0.15579 | 139 | 0.173 | 135 | 0.31032 | 150 | 0.32467 | 144 | 0.449 | 160 | 0.466
[8 empty] | 250.2 | 0.036 |  |  | 120.6 | 0.078 | 134 | 0.093 | 126 | 0.15365 | 140 | 0.168 | 135.9 | 0.30616 | 151 | 0.3205 | 144.9 | 0.444 | 161 | 0.458
[8 empty] | 250.2 | 0.007 |  |  | 121.5 | 0.077 | 135 | 0.093 | 126.9 | 0.15155 | 141 | 0.168 | 136.8 | 0.3021 | 152 | 0.31634 | 145.8 | 0.438 | 162 | 0.452
[8 empty] | 468 | 0.003 |  |  | 122.4 | 0.076 | 136 | 0.093 | 127.8 | 0.14952 | 142 | 0.166 | 137.7 | 0.29811 | 153 | 0.31217 | 146.7 | 0.432 | 163 | 0.45
[8 empty] | 6300 | 0.003 |  |  | 123.3 | 0.075 | 137 | 0.091 | 128.7 | 0.14752 | 143 | 0.165 | 138.6 | 0.29421 | 154 | 0.308 | 147.6 | 0.427 | 164 | 0.441
[12 empty] | 124.2 | 0.074 | 138 | 0.091 | 129.6 | 0.14557 | 144 | 0.16 | 139.5 | 0.29039 | 155 | 0.30384 | 148.5 | 0.421 | 165 | 0.435
[12 empty] | 125.1 | 0.073 | 139 | 0.09 | 130.5 | 0.14365 | 145 | 0.159 | 140.4 | 0.28663 | 156 | 0.30175 | 149.4 | 0.416 | 166 | 0.433
[12 empty] | 126 | 0.073 | 140 | 0.09 | 131.4 | 0.14176 | 146 | 0.158 | 141.3 | 0.28297 | 157 | 0.29967 | 150.3 | 0.411 | 167 | 0.425
[12 empty] | 126.9 | 0.072 | 141 | 0.086 | 132.3 | 0.13993 | 147 | 0.157 | 142.2 | 0.27938 | 158 | 0.29342 | 151.2 | 0.406 | 168 | 0.418
[12 empty] | 127.8 | 0.071 | 142 | 0.085 | 133.2 | 0.13813 | 148 | 0.152 | 143.1 | 0.27586 | 159 | 0.29134 | 152.1 | 0.401 | 169 | 0.416
[12 empty] | 128.7 | 0.07 | 143 | 0.085 | 134.1 | 0.13637 | 149 | 0.152 | 144 | 0.27239 | 160 | 0.28509 | 153 | 0.396 | 170 | 0.41
[12 empty] | 129.6 | 0.069 | 144 | 0.084 | 135 | 0.13464 | 150 | 0.15 | 144.9 | 0.26901 | 161 | 0.283 | 153.9 | 0.391 | 171 | 0.408
[12 empty] | 130.5 | 0.068 | 145 | 0.084 | 135.9 | 0.13295 | 151 | 0.15 | 145.8 | 0.26569 | 162 | 0.283 | 154.8 | 0.386 | 172 | 0.402
[12 empty] | 131.4 | 0.067 | 146 | 0.083 | 136.8 | 0.13129 | 152 | 0.148 | 146.7 | 0.26243 | 163 | 0.27675 | 155.7 | 0.382 | 173 | 0.396
[12 empty] | 132.3 | 0.067 | 147 | 0.083 | 137.7 | 0.12968 | 153 | 0.144 | 147.6 | 0.25923 | 164 | 0.27467 | 156.6 | 0.377 | 174 | 0.391
[12 empty] | 133.2 | 0.066 | 148 | 0.083 | 138.6 | 0.12808 | 154 | 0.143 | 148.5 | 0.25611 | 165 | 0.2705 | 157.5 | 0.373 | 175 | 0.387
[12 empty] | 134.1 | 0.065 | 149 | 0.082 | 139.5 | 0.12653 | 155 | 0.143 | 149.4 | 0.25304 | 166 | 0.26634 | 158.4 | 0.368 | 176 | 0.383
[12 empty] | 135 | 0.064 | 150 | 0.082 | 140.4 | 0.125 | 156 | 0.141 | 150.3 | 0.25003 | 167 | 0.26634 | 159.3 | 0.364 | 177 | 0.379
[12 empty] | 135.9 | 0.064 | 151 | 0.078 | 141.3 | 0.12351 | 157 | 0.14 | 151.2 | 0.24708 | 168 | 0.26009 | 160.2 | 0.36 | 178 | 0.375
[12 empty] | 136.8 | 0.063 | 152 | 0.078 | 142.2 | 0.12202 | 158 | 0.136 | 152.1 | 0.24416 | 169 | 0.258 | 161.1 | 0.356 | 179 | 0.371
[12 empty] | 137.7 | 0.062 | 153 | 0.077 | 143.1 | 0.1206 | 159 | 0.135 | 153 | 0.24131 | 170 | 0.258 | 162 | 0.352 | 180 | 0.366
[12 empty] | 138.6 | 0.061 | 154 | 0.077 | 144 | 0.11918 | 160 | 0.134 | 153.9 | 0.23851 | 171 | 0.25175 | 162.9 | 0.348 | 181 | 0.362
[12 empty] | 139.5 | 0.061 | 155 | 0.076 | 144.9 | 0.11779 | 161 | 0.133 | 154.8 | 0.23576 | 172 | 0.24967 | 163.8 | 0.344 | 182 | 0.358
[12 empty] | 140.4 | 0.06 | 156 | 0.076 | 145.8 | 0.11643 | 162 | 0.133 | 155.7 | 0.23306 | 173 | 0.24967 | 164.7 | 0.34 | 183 | 0.354
[12 empty] | 141.3 | 0.059 | 157 | 0.075 | 146.7 | 0.11509 | 163 | 0.132 | 156.6 | 0.2304 | 174 | 0.24342 | 165.6 | 0.336 | 184 | 0.35
[12 empty] | 142.2 | 0.059 | 158 | 0.075 | 147.6 | 0.11377 | 164 | 0.131 | 157.5 | 0.22779 | 175 | 0.24134 | 166.5 | 0.333 | 185 | 0.35
[12 empty] | 143.1 | 0.058 | 159 | 0.075 | 148.5 | 0.11248 | 165 | 0.127 | 158.4 | 0.22525 | 176 | 0.24134 | 167.4 | 0.329 | 186 | 0.343
[12 empty] | 144 | 0.058 | 160 | 0.075 | 149.4 | 0.11123 | 166 | 0.127 | 159.3 | 0.22274 | 177 | 0.23717 | 168.3 | 0.325 | 187 | 0.341
[12 empty] | 144.9 | 0.057 | 161 | 0.075 | 150.3 | 0.10998 | 167 | 0.126 | 160.2 | 0.22027 | 178 | 0.23509 | 169.2 | 0.322 | 188 | 0.335
[12 empty] | 145.8 | 0.056 | 162 | 0.073 | 151.2 | 0.10877 | 168 | 0.125 | 161.1 | 0.21783 | 179 | 0.233 | 170.1 | 0.318 | 189 | 0.333
[12 empty] | 146.7 | 0.056 | 163 | 0.073 | 152.1 | 0.10758 | 169 | 0.125 | 162 | 0.21545 | 180 | 0.22884 | 171 | 0.315 | 190 | 0.329
[12 empty] | 147.6 | 0.055 | 164 | 0.069 | 153 | 0.10641 | 170 | 0.123 | 162.9 | 0.2131 | 181 | 0.22675 | 171.9 | 0.312 | 191 | 0.327
[12 empty] | 148.5 | 0.055 | 165 | 0.069 | 153.9 | 0.10524 | 171 | 0.119 | 163.8 | 0.21082 | 182 | 0.22467 | 172.8 | 0.308 | 192 | 0.325
[12 empty] | 149.4 | 0.054 | 166 | 0.068 | 154.8 | 0.10411 | 172 | 0.119 | 164.7 | 0.20856 | 183 | 0.22467 | 173.7 | 0.305 | 193 | 0.318
[12 empty] | 150.3 | 0.054 | 167 | 0.068 | 155.7 | 0.103 | 173 | 0.118 | 165.6 | 0.20632 | 184 | 0.2205 | 174.6 | 0.302 | 194 | 0.316
[12 empty] | 151.2 | 0.053 | 168 | 0.068 | 156.6 | 0.10191 | 174 | 0.118 | 166.5 | 0.20415 | 185 | 0.21842 | 175.5 | 0.299 | 195 | 0.312
[12 empty] | 152.1 | 0.052 | 169 | 0.068 | 157.5 | 0.10083 | 175 | 0.116 | 167.4 | 0.20199 | 186 | 0.21634 | 176.4 | 0.296 | 196 | 0.31
[12 empty] | 153 | 0.052 | 170 | 0.068 | 158.4 | 0.099787 | 176 | 0.116 | 168.3 | 0.19987 | 187 | 0.21634 | 177.3 | 0.293 | 197 | 0.308
[12 empty] | 153.9 | 0.051 | 171 | 0.068 | 159.3 | 0.098755 | 177 | 0.116 | 169.2 | 0.1978 | 188 | 0.21217 | 178.2 | 0.29 | 198 | 0.304
[12 empty] | 154.8 | 0.051 | 172 | 0.066 | 160.2 | 0.097749 | 178 | 0.115 | 170.1 | 0.19576 | 189 | 0.21009 | 179.1 | 0.287 | 199 | 0.302
[12 empty] | 155.7 | 0.05 | 173 | 0.066 | 161.1 | 0.096736 | 179 | 0.111 | 171 | 0.19344 | 190 | 0.20939 | 180 | 0.284 | 200 | 0.3
[12 empty] | 156.6 | 0.05 | 174 | 0.066 | 162 | 0.095749 | 180 | 0.111 | 171.9 | 0.19146 | 191 | 0.208 | 180.9 | 0.281 | 201 | 0.296
[12 empty] | 157.5 | 0.05 | 175 | 0.066 | 162.9 | 0.094786 | 181 | 0.11 | 172.8 | 0.18951 | 192 | 0.20661 | 181.8 | 0.278 | 202 | 0.293
[12 empty] | 158.4 | 0.049 | 176 | 0.066 | 163.8 | 0.093822 | 182 | 0.109 | 173.7 | 0.18758 | 193 | 0.20245 | 182.7 | 0.275 | 203 | 0.291
[12 empty] | 159.3 | 0.049 | 177 | 0.066 | 164.7 | 0.092899 | 183 | 0.108 | 174.6 | 0.18571 | 194 | 0.20106 | 183.6 | 0.273 | 204 | 0.287
[12 empty] | 160.2 | 0.048 | 178 | 0.065 | 165.6 | 0.091966 | 184 | 0.108 | 175.5 | 0.18387 | 195 | 0.19967 | 184.5 | 0.27 | 205 | 0.285
[12 empty] | 161.1 | 0.048 | 179 | 0.065 | 166.5 | 0.091073 | 185 | 0.108 | 176.4 | 0.18204 | 196 | 0.19967 | 185.4 | 0.267 | 206 | 0.283
[12 empty] | 162 | 0.047 | 180 | 0.065 | 167.4 | 0.090177 | 186 | 0.107 | 177.3 | 0.18025 | 197 | 0.19411 | 186.3 | 0.265 | 207 | 0.279
[12 empty] | 162.9 | 0.047 | 181 | 0.061 | 168.3 | 0.0893 | 187 | 0.107 | 178.2 | 0.17847 | 198 | 0.19342 | 187.2 | 0.262 | 208 | 0.277
[12 empty] | 163.8 | 0.046 | 182 | 0.061 | 169.2 | 0.088431 | 188 | 0.102 | 179.1 | 0.17673 | 199 | 0.19273 | 188.1 | 0.26 | 209 | 0.275
[12 empty] | 164.7 | 0.046 | 183 | 0.061 | 170.1 | 0.087577 | 189 | 0.102 | 180 | 0.17501 | 200 | 0.19134 | 189 | 0.257 | 210 | 0.275
[12 empty] | 165.6 | 0.046 | 184 | 0.061 | 171 | 0.086749 | 190 | 0.102 | 180.9 | 0.17333 | 201 | 0.18995 | 189.9 | 0.255 | 211 | 0.268
[12 empty] | 166.5 | 0.045 | 185 | 0.06 | 171.9 | 0.085929 | 191 | 0.101 | 181.8 | 0.17166 | 202 | 0.18578 | 190.8 | 0.252 | 212 | 0.266
[12 empty] | 167.4 | 0.045 | 186 | 0.06 | 172.8 | 0.085112 | 192 | 0.101 | 182.7 | 0.17003 | 203 | 0.18509 | 191.7 | 0.25 | 213 | 0.266
[12 empty] | 168.3 | 0.044 | 187 | 0.06 | 173.7 | 0.084315 | 193 | 0.1 | 183.6 | 0.16843 | 204 | 0.18439 | 192.6 | 0.248 | 214 | 0.262
[12 empty] | 169.2 | 0.044 | 188 | 0.059 | 174.6 | 0.083541 | 194 | 0.1 | 184.5 | 0.16683 | 205 | 0.183 | 193.5 | 0.245 | 215 | 0.26
[12 empty] | 170.1 | 0.044 | 500 | 0.05 | 175.5 | 0.082784 | 195 | 0.1 | 185.4 | 0.16526 | 206 | 0.183 | 194.4 | 0.243 | 216 | 0.258
[12 empty] | 171 | 0.043 | 500 | 0.033 | 176.4 | 0.082019 | 196 | 0.1 | 186.3 | 0.16372 | 207 | 0.17745 | 195.3 | 0.241 | 217 | 0.258
[12 empty] | 171.9 | 0.043 | 1000 | 0.033 | 177.3 | 0.081277 | 197 | 0.098 | 187.2 | 0.1622 | 208 | 0.17675 | 196.2 | 0.239 | 218 | 0.252
[12 empty] | 172.8 | 0.043 | 6300 | 0.022 | 178.2 | 0.08054 | 198 | 0.098 | 188.1 | 0.16071 | 209 | 0.17606 | 197.1 | 0.237 | 219 | 0.252
[12 empty] | 250.2 | 0.039 |  |  | 179.1 | 0.079812 | 199 | 0.094 | 189 | 0.15923 | 210 | 0.17467 | 198 | 0.234 | 220 | 0.25
[12 empty] | 250.2 | 0.007 |  |  | 180 | 0.079091 | 200 | 0.094 | 189.9 | 0.15779 | 211 | 0.17467 | 198.9 | 0.232 | 221 | 0.25
[12 empty] | 468 | 0.003 |  |  | 180.9 | 0.0784 | 201 | 0.093 | 190.8 | 0.15635 | 212 | 0.17328 | 199.8 | 0.23 | 222 | 0.243
[12 empty] | 6300 | 0.003 |  |  | 181.8 | 0.077704 | 202 | 0.093 | 191.7 | 0.15494 | 213 | 0.16911 | 200.7 | 0.228 | 223 | 0.243
[16 empty] | 182.7 | 0.077022 | 203 | 0.093 | 192.6 | 0.15354 | 214 | 0.16842 | 201.6 | 0.226 | 224 | 0.241
[16 empty] | 183.6 | 0.076358 | 204 | 0.093 | 193.5 | 0.15217 | 215 | 0.16773 | 202.5 | 0.224 | 225 | 0.241
[16 empty] | 184.5 | 0.07569 | 205 | 0.091 | 194.4 | 0.15081 | 216 | 0.16634 | 203.4 | 0.222 | 226 | 0.235
[16 empty] | 185.4 | 0.075038 | 206 | 0.091 | 195.3 | 0.14948 | 217 | 0.16634 | 204.3 | 0.22 | 227 | 0.235
[16 empty] | 186.3 | 0.074394 | 207 | 0.091 | 196.2 | 0.14818 | 218 | 0.16495 | 205.2 | 0.218 | 228 | 0.233
[16 empty] | 187.2 | 0.073768 | 208 | 0.091 | 197.1 | 0.14689 | 219 | 0.16078 | 206.1 | 0.216 | 229 | 0.233
[16 empty] | 188.1 | 0.07314 | 209 | 0.09 | 198 | 0.14561 | 220 | 0.16009 | 207 | 0.215 | 230 | 0.229
[16 empty] | 189 | 0.07252 | 210 | 0.09 | 198.9 | 0.14436 | 221 | 0.15939 | 207.9 | 0.213 | 231 | 0.227
[16 empty] | 189.9 | 0.071916 | 211 | 0.086 | 199.8 | 0.14311 | 222 | 0.15939 | 208.8 | 0.211 | 232 | 0.225
[16 empty] | 190.8 | 0.071317 | 212 | 0.086 | 200.7 | 0.14189 | 223 | 0.158 | 209.7 | 0.209 | 233 | 0.225
[16 empty] | 191.7 | 0.070735 | 213 | 0.085 | 201.6 | 0.14067 | 224 | 0.158 | 210.6 | 0.207 | 234 | 0.225
[16 empty] | 192.6 | 0.070146 | 214 | 0.085 | 202.5 | 0.13949 | 225 | 0.15661 | 211.5 | 0.206 | 235 | 0.218
[16 empty] | 193.5 | 0.069578 | 215 | 0.085 | 203.4 | 0.13831 | 226 | 0.15245 | 212.4 | 0.204 | 236 | 0.218
[16 empty] | 194.4 | 0.068999 | 216 | 0.084 | 204.3 | 0.13714 | 227 | 0.15175 | 213.3 | 0.202 | 237 | 0.216
[16 empty] | 195.3 | 0.06845 | 217 | 0.084 | 205.2 | 0.13601 | 228 | 0.15106 | 214.2 | 0.201 | 238 | 0.216
[16 empty] | 196.2 | 0.067902 | 218 | 0.083 | 206.1 | 0.13488 | 229 | 0.15106 | 215.1 | 0.199 | 239 | 0.216
[16 empty] | 197.1 | 0.06737 | 219 | 0.083 | 207 | 0.13376 | 230 | 0.14967 | 216 | 0.197 | 240 | 0.21
[16 empty] | 198 | 0.066825 | 220 | 0.083 | 207.9 | 0.13267 | 231 | 0.14967 | 216.9 | 0.196 | 241 | 0.21
[16 empty] | 198.9 | 0.066307 | 221 | 0.083 | 208.8 | 0.13159 | 232 | 0.14828 | 217.8 | 0.194 | 242 | 0.209
[16 empty] | 199.8 | 0.065783 | 222 | 0.083 | 209.7 | 0.13051 | 233 | 0.14759 | 218.7 | 0.192 | 243 | 0.208
[16 empty] | 200.7 | 0.06527 | 223 | 0.083 | 210.6 | 0.12946 | 234 | 0.14412 | 219.6 | 0.191 | 244 | 0.208
[16 empty] | 201.6 | 0.064762 | 224 | 0.082 | 211.5 | 0.12842 | 235 | 0.14342 | 220.5 | 0.189 | 245 | 0.207
[16 empty] | 202.5 | 0.064268 | 225 | 0.082 | 212.4 | 0.1274 | 236 | 0.14273 | 221.4 | 0.188 | 246 | 0.202
[16 empty] | 203.4 | 0.063778 | 226 | 0.081 | 213.3 | 0.12638 | 237 | 0.14273 | 222.3 | 0.186 | 247 | 0.202
[16 empty] | 204.3 | 0.063287 | 227 | 0.078 | 214.2 | 0.12538 | 238 | 0.14134 | 223.2 | 0.185 | 248 | 0.201
[16 empty] | 205.2 | 0.062813 | 228 | 0.078 | 215.1 | 0.12439 | 239 | 0.14134 | 224.1 | 0.183 | 249 | 0.2
[16 empty] | 206.1 | 0.062337 | 229 | 0.078 | 216 | 0.12341 | 240 | 0.13995 | 225 | 0.182 | 250 | 0.2
[16 empty] | 207 | 0.06187 | 230 | 0.077 | 216.9 | 0.12245 | 241 | 0.13995 | 225.9 | 0.18 | 251 | 0.198
[16 empty] | 207.9 | 0.061403 | 231 | 0.077 | 217.8 | 0.12149 | 242 | 0.13578 | 226.8 | 0.179 | 252 | 0.194
[16 empty] | 208.8 | 0.060959 | 232 | 0.076 | 218.7 | 0.12056 | 243 | 0.13508 | 227.7 | 0.178 | 253 | 0.193
[16 empty] | 209.7 | 0.060499 | 233 | 0.076 | 219.6 | 0.11964 | 244 | 0.13508 | 228.6 | 0.176 | 254 | 0.193
[16 empty] | 210.6 | 0.060065 | 234 | 0.076 | 220.5 | 0.11871 | 245 | 0.13439 | 229.5 | 0.175 | 255 | 0.191
[16 empty] | 211.5 | 0.059618 | 235 | 0.076 | 221.4 | 0.1178 | 246 | 0.133 | 230.4 | 0.174 | 256 | 0.191
[16 empty] | 212.4 | 0.059205 | 236 | 0.075 | 222.3 | 0.11692 | 247 | 0.133 | 231.3 | 0.172 | 257 | 0.19
[16 empty] | 213.3 | 0.058774 | 237 | 0.075 | 223.2 | 0.11604 | 248 | 0.133 | 232.2 | 0.171 | 258 | 0.186
[16 empty] | 214.2 | 0.058354 | 238 | 0.075 | 224.1 | 0.11517 | 249 | 0.13162 | 233.1 | 0.17 | 259 | 0.185
[16 empty] | 215.1 | 0.057929 | 239 | 0.075 | 225 | 0.11431 | 250 | 0.13162 | 234 | 0.168 | 260 | 0.184
[16 empty] | 216 | 0.057527 | 240 | 0.075 | 225.9 | 0.11345 | 251 | 0.12745 | 234.9 | 0.167 | 261 | 0.183
[16 empty] | 216.9 | 0.057119 | 241 | 0.075 | 226.8 | 0.1126 | 252 | 0.12745 | 235.8 | 0.166 | 262 | 0.183
[16 empty] | 217.8 | 0.056713 | 242 | 0.073 | 227.7 | 0.11178 | 253 | 0.12676 | 236.7 | 0.165 | 263 | 0.182
[16 empty] | 218.7 | 0.056328 | 243 | 0.073 | 228.6 | 0.11096 | 254 | 0.12606 | 237.6 | 0.164 | 264 | 0.177
[16 empty] | 219.6 | 0.05594 | 244 | 0.073 | 229.5 | 0.11015 | 255 | 0.12606 | 238.5 | 0.162 | 265 | 0.177
[16 empty] | 220.5 | 0.055557 | 245 | 0.073 | 230.4 | 0.10934 | 256 | 0.12467 | 239.4 | 0.161 | 266 | 0.177
[16 empty] | 221.4 | 0.055168 | 246 | 0.069 | 231.3 | 0.10856 | 257 | 0.12467 | 240.3 | 0.16 | 267 | 0.176
[16 empty] | 222.3 | 0.0548 | 247 | 0.069 | 232.2 | 0.10777 | 258 | 0.12467 | 241.2 | 0.159 | 268 | 0.175
[16 empty] | 223.2 | 0.054431 | 248 | 0.069 | 233.1 | 0.10699 | 259 | 0.12467 | 242.1 | 0.158 | 269 | 0.175
[16 empty] | 224.1 | 0.054055 | 249 | 0.068 | 234 | 0.10624 | 260 | 0.12328 | 243 | 0.157 | 270 | 0.173
[16 empty] | 225 | 0.053698 | 250 | 0.068 | 234.9 | 0.10548 | 261 | 0.12258 | 243.9 | 0.156 | 271 | 0.173
[16 empty] | 225.9 | 0.053338 | 251 | 0.068 | 235.8 | 0.10475 | 262 | 0.11911 | 244.8 | 0.154 | 272 | 0.169
[16 empty] | 226.8 | 0.052974 | 252 | 0.068 | 236.7 | 0.104 | 263 | 0.11841 | 245.7 | 0.153 | 273 | 0.168
[16 empty] | 227.7 | 0.052643 | 253 | 0.068 | 237.6 | 0.10328 | 264 | 0.11841 | 246.6 | 0.152 | 274 | 0.168
[16 empty] | 228.6 | 0.052292 | 254 | 0.068 | 238.5 | 0.10256 | 265 | 0.11772 | 247.5 | 0.151 | 275 | 0.166
[16 empty] | 229.5 | 0.05195 | 255 | 0.068 | 239.4 | 0.10185 | 266 | 0.11772 | 248.4 | 0.15 | 276 | 0.166
[16 empty] | 230.4 | 0.051604 | 256 | 0.068 | 240.3 | 0.10115 | 267 | 0.11634 | 249.3 | 0.149 | 277 | 0.166
[16 empty] | 231.3 | 0.051283 | 257 | 0.066 | 241.2 | 0.10045 | 268 | 0.11634 | 250.2 | 0.148 | 278 | 0.165
[16 empty] | 232.2 | 0.050942 | 258 | 0.066 | 242.1 | 0.099753 | 269 | 0.11634 | 250.2 | 0.007 | 279 | 0.161
[16 empty] | 233.1 | 0.050616 | 259 | 0.066 | 243 | 0.099077 | 270 | 0.11634 | 468 | 0.003 | 280 | 0.161
[16 empty] | 234 | 0.0503 | 260 | 0.066 | 243.9 | 0.098407 | 271 | 0.11496 | 6300 | 0.003 | 281 | 0.16
[16 empty] | 234.9 | 0.049979 | 261 | 0.066 | 244.8 | 0.097749 | 272 | 0.11496 |  |  | 282 | 0.159
[16 empty] | 235.8 | 0.049679 | 262 | 0.066 | 245.7 | 0.097086 | 273 | 0.11426 |  |  | 283 | 0.159
[16 empty] | 236.7 | 0.049361 | 263 | 0.066 | 246.6 | 0.096437 | 274 | 0.11079 |  |  | 284 | 0.158
[16 empty] | 237.6 | 0.049056 | 264 | 0.066 | 247.5 | 0.095798 | 275 | 0.11079 |  |  | 285 | 0.158
[16 empty] | 238.5 | 0.048758 | 265 | 0.066 | 248.4 | 0.095164 | 276 | 0.1101 |  |  | 286 | 0.158
[16 empty] | 239.4 | 0.048459 | 266 | 0.065 | 249.3 | 0.094533 | 277 | 0.1101 |  |  | 287 | 0.157
[16 empty] | 240.3 | 0.048156 | 267 | 0.065 | 250.2 | 0.093917 | 278 | 0.1094 |  |  | 288 | 0.152
[16 empty] | 241.2 | 0.047868 | 268 | 0.065 | 250.2 | 0.0072687 | 279 | 0.1094 |  |  | 289 | 0.152
[16 empty] | 242.1 | 0.04757 | 269 | 0.065 | 468 | 0.003 | 280 | 0.108 |  |  | 290 | 0.152
[16 empty] | 243 | 0.047293 | 270 | 0.065 | 6300 | 0.003 | 281 | 0.108 |  |  | 291 | 0.151
[16 empty] | 243.9 | 0.047005 | 271 | 0.064 |  |  | 282 | 0.108 |  |  | 292 | 0.151
[16 empty] | 244.8 | 0.046728 | 500 | 0.052 |  |  | 283 | 0.108 |  |  | 293 | 0.15
[16 empty] | 245.7 | 0.046454 | 500 | 0.033 |  |  | 284 | 0.108 |  |  | 294 | 0.15
[16 empty] | 246.6 | 0.046177 | 1000 | 0.033 |  |  | 285 | 0.1066 |  |  | 295 | 0.15
[16 empty] | 247.5 | 0.045908 | 6300 | 0.022 |  |  | 286 | 0.1066 |  |  | 296 | 0.148
[16 empty] | 248.4 | 0.045636 |  |  |  |  | 287 | 0.10243 |  |  | 297 | 0.144
[16 empty] | 249.3 | 0.045374 |  |  |  |  | 288 | 0.10243 |  |  | 298 | 0.143
[16 empty] | 250.2 | 0.045117 |  |  |  |  | 289 | 0.10243 |  |  | 299 | 0.143
[16 empty] | 250.2 | 0.0072687 |  |  |  |  | 290 | 0.10174 |  |  | 300 | 0.061
[16 empty] | 468 | 0.003 |  |  |  |  | 291 | 0.10174 |  |  | 500 | 0.057
[16 empty] | 6300 | 0.003 |  |  |  |  | 292 | 0.10105 |  |  | 500 | 0.033
[22 empty] | 293 | 0.10105 |  |  | 1000 | 0.033
[22 empty] | 294 | 0.10105 |  |  | 6300 | 0.022
[22 empty] | 295 | 0.099673
[22 empty] | 296 | 0.099673
[22 empty] | 297 | 0.099673
[22 empty] | 298 | 0.099673
[22 empty] | 299 | 0.099673
[22 empty] | 300 | 0.060901
[22 empty] | 500 | 0.057
[22 empty] | 500 | 0.033
[22 empty] | 1000 | 0.033
[22 empty] | 6300 | 0.022